## Full Mapping Table
BACnet Exchange Requirement
Header Section | [6 empty] | BACnet Object Type
Name |  | ER_Exchange Premilinary BAS Model |  |  |  |  | user defined concept template
Identifier |  | BACnet_ER_0001 |  |  |  |  | Custom defined Properties in Pset
Change Log
<2018-03-20> |  | Created 25/54 BACnet objects | Stang93@gatech.edu
Project Stage | 31-10 00 00 | Inception Phase
| 31-20 00 00 | Conceptualization Phase
| 31-30 00 00 | Criteria Definition Phase
| 31-40 00 00 | Design Phase |  | √
| 31-50 00 00 | Coordination Phase |  | √
| 31-60 00 00 | Implementation Phase |  | √
| 31-70 00 00 | Handover Phase |  | √
| 31-80 00 00 | Operations Phase |  | √
| 31-90 00 00 | Closure Phase
Overview
Scope
The scope of this exchange requirement is the exchange of Building Automation System (BAS) design information between other project design roles. The BAS components should be designed using BACnet protocol including objects, attributes and services. The exchange requirement also includes the need for shape, size and location of components.
General Discription
This exchange requirement allows BAS component information represented in IFC standards to be shared among various project design roles including architects, structural engineer and MEP engineers. The BAS component information can also be shared throughout several design interactions from conceptual design to production information. The BAS components should be designed using BACnet protocol including objects and attributes. The exchange requirement also includes the need for shape, composition and location of components.
Information Description
Information provided through this exchange requirement includes: • BAS components objects, attributes • Shape representation of components • Location and orientation of occurrences of components • connectivity and composition of components
Information Requirment
Information Unit |  | Description | Entity/Pset/Functional Part | Man | Rec | Opt | Mapped Concept
BACnet Analog Input Object Type |  |  | IfcController
| Object Geometric Representation | Geometric representation of the object | IfcProduct.Representation->IfcProductDefinitionShape |  | √ |  | Box Geometry; FootPrint Annotation Geometry
| Object Placement | placement of the object | IfcProduct.ObjectPlacement->IfcObjectPlacement |  | √ |  | Product local placement
| Object Contained in Space | the object contained in space | IfcElement.ContainedInStructure ->IfcRelContainedInSpatialStructure |  | √ |  | Spatial Containment
| Object Connected From | other objects connection | IfcElement.ConnectedFrom->IfcRelConnectsElements |  | √ |  | Path Connectivity
| Decomposes | which device is the object decomposed by | IfcObjectDefinition.Decomposes->IfcRelAggregates |  | √ |  | Object Definition Composition
| Object Identifier | This property, of type BACnetObjectIdentifier, is a numeric code that is used to identify the object. It shall be unique within the BACnect device that maintains it | IfcControllort.GlobalId->IfcGloballyUniqueId | √ |  |  | Software Identity
| Object Name | This property, of type CharacterString, shall represent a name for the object that is unique within the BACnet device that maintains it. The minimum length of the string shall be one character. The set of characters used in the Object_Name shall be restricted to printable characters | IfcControllor.Name->IfcLable | √ |  |  | Object User Identity
| Object Type | Indicates membership in a particular object type class. The value of this property shall be ANALOG_INPUT,Predefined Type =MULTIPOSITION | IfcController.PredefinedType->IfcControllerTypeEnum | √ |  |  | BACnet Controllor Predefined Type; Object Predefined Type
| Present Value | This property, of type REAL, indicates the current value, in engineering units, of the input being measured. ThePresent_Value property shall be writable when Out_Of_Service is TRUE | Pset_ControllerTypeMultiPosition.Value->IfcInteger | √ |  |  | PropertySets for Objects
| Description | Other description of object | IfcRoot.Description->IfcText |  |  | √ | -
| Status Flags | This property, of type BACnetStatusFlags, represents four Boolean flags that indicate the general “health” of object. PEnum_BACnetStatusFlagsEnum = ENUMERATION OF( IN_ALARM, FAULT, OVERRIDEN, OUT_OF_SERVICE); | Pset_BACnetAnalogInputObject.StatusFlags ->IfcLabel:: PEnum_BACnetStatusFlag | √ |  |  | PropertySets for Objects
| Event State | The Event_State property, of type BACnetEventState, is included in order to provide a way to determine whether this object has an active event state associated with it. PEnum_BACnetEventStateEnum = ENUMERATION OF( NORMAL, OFFNORMAL, FAULT); | Pset_BACnetAnalogInputObject.EventState ->IfcLabel:: PEnum_BACnetEventState | √ |  |  | PropertySets for Objects
| Out of Service | The Out_Of_Service property, of type BOOLEAN, is an indication whether (TRUE) or not (FALSE) the physical input that the object represents is not in service. | Pset_BACnetAnalogInputObject.OutOfService ->IfcBoolean | √ | ` |  | PropertySets for Objects
| Units | This property, of type BACnetEngineeringUnits, indicates the measurement units of this object. | Pset_BACnetAnalogInputObject.Units ->IfcLabel | √ |  |  | PropertySets for Objects
| Property List | This read-only property is a BACnetARRAY of property identifiers, one property identifier for each property that exists within the object. | IfcPropertySet.HasPropertites->IfcProperty | √ |  |  | PropertySets for Objects
| Tags | tags related to the object | IfcElement.Tag->IfcIdentifier |  |  | √ | Element Occurrence Attributes
BACnet Analog Output Object Type |  |  | IfcController
| Object Geometric Representation |  | IfcProduct.Representation->IfcProductDefinitionShape |  | √ |  | Box Geometry; FootPrint Annotation Geometry
| Object Placement |  | IfcProduct.ObjectPlacement->IfcObjectPlacement |  | √ |  | Product local placement
| Object Contained in Space | the object contained in space | IfcElement.ContainedInStructure ->IfcRelContainedInSpatialStructure |  | √ |  | Spatial Containment
| Object Connected From |  | IfcElement.ConnectedFrom->IfcRelConnectsElements |  | √ |  | Path Connectivity
| Decomposes | which device is the object decomposed by | IfcObjectDefinition.Decomposes->IfcRelAggregates |  | √ |  | Object Definition Composition
| Object Identifier |  | IfcRoot.GlobalId->IfcGloballyUniqueId | √ |  |  | Software Identity
| Object Name |  | IfcRoot.Name->IfcLable | √ |  |  | Object User Identity
| Object Type | Predefined Type =MULTIPOSITION | IfcController.PredefinedType->IfcControllerTypeEnum | √ |  |  | BACnet Controllor Predefined Type; Object Predefined Type
| Present Value |  | Pset_ControllerTypeMultiPosition.Value->IfcInteger | √ |  |  | PropertySets for Objects
| Description |  | IfcRoot.Description->IfcText |  |  | √ | -
| Status Flags | PEnum_BACnetStatusFlags = ENUMERATION OF( IN_ALARM, FAULT, OVERRIDEN, OUT_OF_SERVICE); | Pset_BACnetAnalogOutputObject.StatusFlags ->IfcLabel:: PEnum_BACnetStatusFlag | √ |  |  | PropertySets for Objects
| Event State | PEnum_BACnetEventState = ENUMERATION OF( NORMAL, OFFNORMAL, FAULT); | Pset_BACnetAnalogOutputObject.EventState ->IfcLabel:: PEnum_BACnetEventState | √ |  |  | PropertySets for Objects
| Out of Service |  | Pset_BACnetAnalogOutputObject.OutOfService ->IfcBoolean | √ | ` |  | PropertySets for Objects
| Units |  | Pset_BACnetAnalogOutputObject.Units ->IfcLabel | √ |  |  | PropertySets for Objects
| Priority Array | array of BACnetPriorityValue::=CHOICE of (NULL,REAL,ENUMERATED,UNSIGNED, INTEGER, DOUBLE,TIME,CHARATERSTRING, OCETESTRING, BIT STRING, DATE, BACNETOBJECTIDENTIFIER, ABSTRACT-SYNTAX.&TYPE, BACNETDATETIME) | Pset_BACnetAnalogOutputObject.PriorityArray ->IfcLabel:: PEnum_BACnetPriorityValue | √ |  |  | PropertySets for Objects
| Relinquish Default | This property is the default value to be used for the Present_Value property when all command priority values in the Priority_Array property have a NULL value. | Pset_BACnetAnalogOutputObject.RelinquishDefault->IfcReal | √ |  |  | PropertySets for Objects
| Property List |  | IfcPropertySet.HasPropertites->IfcProperty | √ |  |  | PropertySets for Objects
| Current Command Priority | Indicates the currently active priority, The value of this property shall be equal to the index of the entry in the Priority_Array from which the Present_Value’s value has been taken. If Present_Value has taken on the value of Relinquish_Default, this property shall have the value Null. | Pset_BACnetAnalogOutputObject.CurrentCommandPriority->IfcInteger | √ |  |  | PropertySets for Objects
| Tags |  | IfcElement.Tag->IfcIdentifier |  |  | √ | Element Occurrence Attributes
BACnet Analog Value Object Type |  |  | IfcController
| Object Geometric Representation |  | IfcProduct.Representation->IfcProductDefinitionShape |  | √ |  | Box Geometry; FootPrint Annotation Geometry
| Object Placement |  | IfcProduct.ObjectPlacement->IfcObjectPlacement |  | √ |  | Product local placement
| Object Contained in Space | the object contained in space | IfcElement.ContainedInStructure ->IfcRelContainedInSpatialStructure |  | √ |  | Spatial Containment
| Object Connected From |  | IfcElement.ConnectedFrom->IfcRelConnectsElements |  | √ |  | Path Connectivity
| Decomposes | which device is the object decomposed by | IfcObjectDefinition.Decomposes->IfcRelAggregates |  | √ |  | Object Definition Composition
| Object Identifier |  | IfcRoot.GlobalId->IfcGloballyUniqueId | √ |  |  | Software Identity
| Object Name |  | IfcRoot.Name->IfcLable | √ |  |  | Object User Identity
| Object Type | Predefined Type =MULTIPOSITION | IfcController.PredefinedType->IfcControllerTypeEnum | √ |  |  | BACnet Controllor Predefined Type; Object Predefined Type
| Present Value |  | Pset_ControllerTypeMultiPosition.Value->IfcInteger | √ |  |  | PropertySets for Objects
| Description |  | IfcRoot.Description->IfcText |  |  | √ | -
| Status Flags | PEnum_BACnetStatusFlags = ENUMERATION OF( IN_ALARM, FAULT, OVERRIDEN, OUT_OF_SERVICE); | Pset_BACnetAnalogValueObject.StatusFlags ->IfcLabel:: PEnum_BACnetStatusFlag | √ |  |  | PropertySets for Objects
| Event State | PEnum_BACnetEventState = ENUMERATION OF( NORMAL, OFFNORMAL, FAULT); | Pset_BACnetAnalogValueObject.EventState ->IfcLabel:: PEnum_BACnetEventState | √ |  |  | PropertySets for Objects
| Out of Service |  | Pset_BACnetAnalogValueObject.OutOfService ->IfcBoolean | √ | ` |  | PropertySets for Objects
| Units |  | Pset_BACnetAnalogInputObject.Units ->IfcLabel | √ |  |  | PropertySets for Objects
| Property List |  | IfcPropertySet | √ |  |  | PropertySets for Objects
| Tags |  | IfcElement.Tag->IfcIdentifier |  |  | √ | Element Occurrence Attributes
BACnet Averaging Object Type |  |  | IfcController, predefined type=FLOATING
| Object Geometric Representation |  | IfcProduct.Representation->IfcProductDefinitionShape |  | √ |  | Box Geometry; FootPrint Annotation Geometry
| Object Placement |  | IfcProduct.ObjectPlacement->IfcObjectPlacement |  | √ |  | Product local placement
| Object Contained in Space | the object contained in space | IfcElement.ContainedInStructure ->IfcRelContainedInSpatialStructure |  | √ |  | Spatial Containment
| Object Connected From |  | IfcElement.ConnectedFrom->IfcRelConnectsElements |  | √ |  | Path Connectivity
| Decomposes | which device is the object decomposed by | IfcObjectDefinition.Decomposes->IfcRelAggregates |  | √ |  | Object Definition Composition
| Object Identifier |  | IfcRoot.GlobalId->IfcGloballyUniqueId | √ |  |  | Software Identity
| Object Name |  | IfcRoot.Name->IfcLable | √ |  |  | Object User Identity
| Object Type | Predefined Type =FLOATING | IfcController.PredefinedType->IfcControllerTypeEnum | √ |  |  | BACnet Controllor Predefined Type; Object Predefined Type
| Description |  | IfcRoot.Description->IfcText |  |  | √ | -
| Minimun value |  | Pset_ControllerTypeFloating.Range ->IfcPropertyBoundedValue.LowerBoundValue::IfcReal | √ |  |  | PropertySets for Objects
| Average Value |  | Pset_ControllerTypeFloating.Value->IfcReal | √ |  |  | PropertySets for Objects
| Maximun Value |  | Pset_ControllerTypeFloating.Range ->IfcPropertyBoundedValue.UpperBoundValue::IfcReal | √ |  |  | PropertySets for Objects
| Attempted Samples | This property, of type Unsigned, indicates the number of samples that have been attempted to be collected for the current window. | Pset_BACnetAveragingObject.AttemptedSamples ->IfcInteger | √ |  |  | PropertySets for Objects
| Valid Samples | This read-only property, of type Unsigned, indicates the number of samples that have been successfully collected for the current window. | Pset_BACnetAveragingObject.ValidSamples ->IfcInteger | √ |  |  | PropertySets for Objects
| Object Property Reference | reference to other BACnet objects | IfcProduct.ReferencedBy ->IfcRelAssignsToProduct.RelatedObject->IfcObject IfcObject.IsDefinedBy->IfcRelDefinesByProperties.RelatedPropertyDefinition -> IfcPropertySet | √ |  |  | Produce assignment and Property Sets for Objects
| Window Interval |  | Pset_BACnetAveragingObject.WindowInterval ->IfcTimeMeasure | √ |  |  | PropertySets for Objects
| Window Sample |  | Pset_BACnetAveragingObject.WindowSamples ->IfcInteger | √ |  |  | PropertySets for Objects
| Property List |  | IfcPropertySet | √ |  |  | PropertySets for Objects
| Tags |  | IfcElement.Tag->IfcIdentifier |  |  | √ | Element Occurrence Attributes
BACnet Binary Input Object Type |  |  | IfcController
| Object Geometric Representation |  | IfcProduct.Representation->IfcProductDefinitionShape |  | √ |  | Box Geometry; FootPrint Annotation Geometry
| Object Placement |  | IfcProduct.ObjectPlacement->IfcObjectPlacement |  | √ |  | Product local placement
| Object Contained in Space | the object contained in space | IfcElement.ContainedInStructure ->IfcRelContainedInSpatialStructure |  | √ |  | Spatial Containment
| Object Connected From |  | IfcElement.ConnectedFrom->IfcRelConnectsElements |  | √ |  | Path Connectivity
| Decomposes | which device is the object decomposed by | IfcObjectDefinition.Decompose->IfcRelAggregates |  | √ |  | Object Definition Composition
| Object Identifier |  | IfcRoot.GlobalId->IfcGloballyUniqueId | √ |  |  | Software Identity
| Object Name |  | IfcRoot.Name->IfcLable | √ |  |  | Object User Identity
| Object Type | Predefined Type =MULTIPOSITION | IfcController.PredefinedType->IfcControllerTypeEnum | √ |  |  | BACnet Controllor Predefined Type; Object Predefined Type
| Present Value |  | Pset_ControllerTypeMultiPosition.Value->IfcInteger | √ |  |  | PropertySets for Objects
| Description |  | IfcRoot.Description->IfcText |  |  | √ | -
| Status Flags | PEnum_BACnetStatusFlagsEnum = ENUMERATION OF( IN_ALARM, FAULT, OVERRIDEN, OUT_OF_SERVICE); | Pset_BACnetBinaryInputObject.StatusFlags ->IfcLabel:: PEnum_BACnetStatusFlag | √ |  |  | PropertySets for Objects
| Event State | PEnum_BACnetEventStateEnum = ENUMERATION OF( NORMAL, OFFNORMAL, FAULT); | Pset_BACnetBinaryInputObject.EventState ->IfcLabel:: PEnum_BACnetEventState | √ |  |  | PropertySets for Objects
| Out of Service |  | Pset_BACnetBinaryInputObject.OutOfService ->IfcBoolean | √ | ` |  | PropertySets for Objects
| Polarity | PEnum_BACnetPolarity = ENUMERATION OF( NORMAL, REVERSE); | Pset_BACnetBinaryInputObject.EventState ->IfcLabel:: PEnum_BACnetPolarity | √ |  |  | PropertySets for Objects
| Property List |  | IfcPropertySet | √ |  |  | PropertySets for Objects
| Tags |  | IfcElement.Tag->IfcIdentifier |  |  | √ | Element Occurrence Attributes
BACnet Binary Output Object Type |  |  | IfcController
| Object Geometric Representation |  | IfcProduct.Representation::IfcProductDefinitionShape |  | √ |  | Box Geometry; FootPrint Annotation Geometry
| Object Placement |  | IfcProduct.ObjectPlacement::IfcObjectPlacement |  | √ |  | Product local placement
| Object Contained in Space | the object contained in space | IfcElement.ContainedInStructure::IfcRelContainedInSpatialStructure |  | √ |  | Spatial Containment
| Object Connected From |  | IfcElement.ConnectedFrom::IfcRelConnectsElements |  | √ |  | Path Connectivity
| Decomposes | which device is the object decomposed by | IfcObjectDefinition.Decomposes::IfcRelAggregates |  | √ |  | Object Definition Composition
| Object Identifier |  | IfcRoot.GlobalId::IfcGloballyUniqueId | √ |  |  | Software Identity
| Object Name |  | IfcRoot.Name::IfcLable | √ |  |  | Object User Identity
| Object Type | Predefined Type =MULTIPOSITION | IfcController.PredefinedType::IfcControllerTypeEnum | √ |  |  | BACnet Controllor Predefined Type; Object Predefined Type
| Present Value |  | Pset_ControllerTypeMultiPosition.Value::IfcInteger | √ |  |  | PropertySets for Objects
| Description |  | IfcRoot.Description::IfcText |  |  | √ | -
| Status Flags | PEnum_BACnetStatusFlags = ENUMERATION OF( IN_ALARM, FAULT, OVERRIDEN, OUT_OF_SERVICE); | Pset_BACnetBinaryOutputObject.StatusFlags ->IfcLabel:: PEnum_BACnetStatusFlag | √ |  |  | PropertySets for Objects
| Event State | PEnum_BACnetEventState = ENUMERATION OF( NORMAL, OFFNORMAL, FAULT); | Pset_BACnetBinaryOutputObject.EventState ->IfcLabel:: PEnum_BACnetEventState | √ |  |  | PropertySets for Objects
| Out of Service |  | Pset_BACnetBinaryOutputObject.OutOfService ->IfcBoolean | √ | ` |  | PropertySets for Objects
| Polarity | PEnum_BACnetPolarity = ENUMERATION OF( NORMAL, REVERSE); | Pset_BACnetBinaryOutputObject.EventState ->IfcLabel:: PEnum_BACnetPolarity | √ |  |  | PropertySets for Objects
| Priority Array | array of BACnetPriorityValue::=CHOICE of (NULL,REAL,ENUMERATED,UNSIGNED, INTEGER, DOUBLE,TIME,CHARATERSTRING, OCETESTRING, BIT STRING, DATE, BACNETOBJECTIDENTIFIER, ABSTRACT-SYNTAX.&TYPE, BACNETDATETIME) | Pset_BACnetBinaryOutputObject.PriorityArray ->IfcLabel:: PEnum_BACnetPriorityValue | √ |  |  | PropertySets for Objects
| Relinquish Default | This property is the default value to be used for the Present_Value property when all command priority values in the Priority_Array property have a NULL value. | Pset_BACnetBinaryOutputObject.RelinquishDefault->IfcReal | √ |  |  | PropertySets for Objects
| Property List |  | IfcPropertySet.HasPropertites->IfcProperty | √ |  |  | PropertySets for Objects
| Current Command Priority | Indicates the currently active priority, The value of this property shall be equal to the index of the entry in the Priority_Array from which the Present_Value’s value has been taken. If Present_Value has taken on the value of Relinquish_Default, this property shall have the value Null. | Pset_BACnetBinaryOutputObject.CurrentCommandPriority->IfcInteger | √ |  |  | PropertySets for Objects
| Tags |  | IfcElement.Tag->IfcIdentifier |  |  | √ | Element Occurrence Attributes
BACnet Binary Value Object Type |  |  | IfcController
| Object Geometric Representation |  | IfcProduct.Representation->IfcProductDefinitionShape |  | √ |  | Box Geometry; FootPrint Annotation Geometry
| Object Placement |  | IfcProduct.ObjectPlacement->IfcObjectPlacement |  | √ |  | Product local placement
| Object Contained in Space | the object contained in space | IfcElement.ContainedInStructure ->IfcRelContainedInSpatialStructure |  | √ |  | Spatial Containment
| Object Connected From |  | IfcElement.ConnectedFrom->IfcRelConnectsElements |  | √ |  | Path Connectivity
| Decomposes | which device is the object decomposed by | IfcObjectDefinition.Decomposes->IfcRelAggregates |  | √ |  | Object Definition Composition
| Object Identifier |  | IfcRoot.GlobalId->IfcGloballyUniqueId | √ |  |  | Software Identity
| Object Name |  | IfcRoot.Name->IfcLable | √ |  |  | Object User Identity
| Object Type | Predefined Type =MULTIPOSITION | IfcController.PredefinedType->IfcControllerTypeEnum | √ |  |  | Controllor Predefined Type; Object Predefined Type
| Present Value |  | Pset_ControllerTypeMultiPosition.Value->IfcInteger | √ |  |  | PropertySets for Objects
| Description |  | IfcRoot.Description->IfcText |  |  | √ | -
| Status Flags | PEnum_BACnetStatusFlags = ENUMERATION OF( IN_ALARM, FAULT, OVERRIDEN, OUT_OF_SERVICE); | Pset_BACnetBinaryValueObject.StatusFlags ->IfcLabel:: PEnum_BACnetStatusFlag | √ |  |  | PropertySets for Objects
| Event State | PEnum_BACnetEventState = ENUMERATION OF( NORMAL, OFFNORMAL, FAULT); | Pset_BACnetBinaryValueObject.EventState ->IfcLabel:: PEnum_BACnetEventState | √ |  |  | PropertySets for Objects
| Out of Service |  | Pset_BACnetBinaryValueObject.OutOfService ->IfcBoolean | √ | ` |  | PropertySets for Objects
| Property List |  | IfcPropertySet | √ |  |  | PropertySets for Objects
| Tags |  | IfcElement.Tag->IfcIdentifier |  |  | √ | Element Occurrence Attributes
BACnet Calender Object Type |  |  | IfcControllor assgined to IfcWorkCalender |  |  |  |  | no custon pset
| Has Assignment |  | IfcObjectDefinition.HasAssignment->IfcRelAssignsToControl | √ |  |  | BACnet-Controller Assign to Work Calender
| Object Geometric Representation |  | IfcProduct.Representation->IfcProductDefinitionShape |  | √ |  | Box Geometry; FootPrint Annotation Geometry
| Object Placement |  | IfcProduct.ObjectPlacement->IfcObjectPlacement |  | √ |  | Product local placement
| Object Contained in Space | the object contained in space | IfcElement.ContainedInStructure ->IfcRelContainedInSpatialStructure |  | √ |  | Spatial Containment
| Object Connected From |  | IfcElement.ConnectedFrom->IfcRelConnectsElements |  | √ |  | Path Connectivity
| Decomposes | which device is the object decomposed by | IfcObjectDefinition.Decomposes->IfcRelAggregates |  | √ |  | Object Definition Composition
| Object Identifier |  | IfcRoot.GlobalId->IfcGloballyUniqueId | √ |  |  | Software Identity
| Object Name |  | IfcRoot.Name->IfcLable | √ |  |  | Object User Identity
| Object Type | Predefined Type =TWOPOSITION， TwoPositionType=CALENDAR | IfcController.PredefinedType->IfcControllerTypeEnum | √ |  |  | BACnet Controllor Predefined Type; Object Predefined Type
| Present Value | This property, of type BOOLEAN, indicates the current value of the calendar: TRUE if the current date is in the Date_List and FALSE if it is not. | Pset_ControllerTypeTwoPosition.Value->IfcBoolean | √ |  |  | PropertySets for Objects
| Description |  | IfcRoot.Description->IfcText |  |  | √ | -
| Date List | This property is a BACnetLIST of BACnetCalendarEntry, each of which is either a specific date or date pattern (Date), range of dates (BACnetDateRange), or month/week-of-month/day-of-week specification (BACnetWeekNDay). | IfcWorkCalender.WorkingTime->IfcWorkTime | √ |  |  | BACnet Controllor assign to Work Calender
| Property List |  | IfcPropertySet | √ |  |  | PropertySets for Objects
| Tags |  | IfcElement.Tag->IfcIdentifier |  |  | √ | Element Occurrence Attributes
BACnet Command Object Type |  |  | IfcProcedure assigned to IfcControllor
| Has Assignment |  | IfcProcedure.HasAssignments ->IfcRelAssignsToControl.RelatedObjects ->IfcObject | √ |  |  | BACnet-Procedure Assign to Controller
| Decomposes | which device is the object decomposed by | IfcObjectDefinition.Decomposes->IfcRelAggregates |  | √ |  | Object Definition Composition
| Object Name |  | IfcRoot.Name->IfcLable | √ |  |  | Software Identity
| Object Idenfifier |  | IfcRoot.GlobalId->IfcGloballyUniqueId | √ |  |  | Object User Identity
| Object Type | IfcProcedure having PredefinedType=CALIBRATION, and assigned to IfcController having PredefinedType=NOTDEFINED | IfcProcedure.PredefinedType->IfcProcedureTypeEnum | √ |  |  | BACnet-Procedure Predefined Type; Object Predefined Type
| Present Value | This property, of type Unsigned, indicates which action the Command object is to take or has already taken.The Present_Value may be written to with any value from 0 to the maximum number of actions supported by the Action property. | Pset-BACnetCommandObject.PresentValue->IfcInteger | √ |  |  | PropertySets for Objects
| Description |  | IfcRoot.Description->IfcText |  |  | √
| In Process | This property, of type BOOLEAN, shall be set to TRUE when a value is written to the Present_Value property. | Pset-BACnetCommandObject.InProcess->IfcBoolean | √ |  |  | PropertySets for Objects
| All Writes Successful | This property, of type BOOLEAN, indicates the success or failure of the sequence of actions that are triggered when the Present_Value property is written to. | Pset-BACnetCommandObject.AllWritesSuccessful->IfcBoolean | √ |  |  | PropertySets for Objects
| Action | This property, of type BACnetARRAY of BACnetActionList, specifies an array of "action lists." These action lists are indexed by the value that is written to the Present_Value property. | Pset-BACnetCommandObject.Action->IfcInteger | √ |  |  | PropertySets for Objects
| Property List |  | IfcPropertySet | √ |  |  | PropertySets for Objects
BACnet Device Object Type |  |  | IfcController
| Object Geometric Representation |  | IfcProduct.Representation->IfcProductDefinitionShape |  | √ |  | Box Geometry; FootPrint Annotation Geometry
| Object Placement |  | IfcProduct.ObjectPlacement->IfcObjectPlacement |  | √ |  | Product local placement
| Object Contained in Space | the object contained in space | IfcElement.ContainedInStructure ->IfcRelContainedInSpatialStructure |  | √ |  | Spatial Containment
| Object Connected From |  | IfcElement.ConnectedFrom->IfcRelConnectsElements |  | √ |  | Path Connectivity
| Object Quantity | Idenfity the number of Device in project | IfcObject.IsDefinedBy->IfcElementQuantity |  | √ |  | Quantity Set
| Object Identifier |  | IfcRoot.GlobalId->IfcGloballyUniqueId | √ |  |  | Software Identity
| Object Name |  | IfcRoot.Name->IfcLable | √ |  |  | Object User Identity
| Object Type | Predefined Type =PROGRAMABLE | IfcController.PredefinedType->IfcControllerTypeEnum | √ |  |  | BACnet Controllor Predefined Type; Object Predefined Type
| System Status | This property, of type BACnetDeviceStatus, reflects the current physical and logical status of the BACnet device. The values that may be taken on by this property are: PEnum_BACnetDeviceStatus = ENUMERATION OF( OPERATIONAL, OPERATIONAL_READ_ONLY, DOWNLOAD_REQUIRED, DOWNLOAD_IN_PROGRESS, NON_OPERATIONAL, BACKUP_IN_PROGRESS) | Pset_BACnetDeviceObject.SystemStatus ->IfcLabel::Penum_BACnetDeviceStatus | √ |  |  | PropertySets for Objects
| Vendor Name | This property, of type CharacterString, identifies the manufacturer of the BACnet device. | Pset_ManufacturereTypeInformation.Manufactuerer->IfcLabel | √ |  |  | PropertySets for Objects
| Vendor Identifier | This read-only property, of type Unsigned16, is a unique vendor identification code, assigned by ASHRAE, which is used to distinguish proprietary extensions to the protocol. | Pset_BACnetDeviceObject.VenderIdentifier ->IfcIdentifier | √ |  |  | PropertySets for Objects
| Model Name | This read-only property, of type CharacterString, is assigned by the vendor to represent the model of the BACnet device | Pset_ManufacturereTypeInformation.ModelLabel::IfcLabel | √ |  |  | PropertySets for Objects
| Firmware Revision | This property, of type CharacterString, is assigned by the vendor to represent the level of firmware installed in the BACnet device. | Pset_ControllorTypeProgrammable.FirmwareVersion:: IfcPropertySingleValue::IfcLabel | √ |  |  | PropertySets for Objects
| Application Software Version | This property, of type CharacterString, identifies the version of application software installed in the machine. The content of this string is a local matter, but it could be a date-and-time stamp, a programmer's name, a host file version number, etc | Pset_ControllorTypeProgrammable.SoftwareVersion::IfcPropertySingleValue::IfcLabel | √ |  |  | PropertySets for Objects
| Protocol Version | This property, of type Unsigned, represents the version of the BACnet protocol supported by this BACnet device. Every major revision of BACnet shall increase this version number by one. The initial release of BACnet shall be version 1. | Pset_BACnetDeviceObject.ProtocolVersion ->IfcText | √ |  |  | PropertySets for Objects
| Protocol Revision | This property, of type Unsigned, shall indicate the minor revision level of the BACnet standard. This value shall start at 1 and be incremented for any substantive change(s) to the BACnet standard that affect device communication or behavior. This value shall revert to zero upon each change to the Protocol_Version property. Changes to the values for Protocol_Version and Protocol_Revision are recorded in the History of Revisions at the end of this standard. | Pset_BACnetDeviceObject.ProtocolRevision ->IfcReal | √ |  |  | PropertySets for Objects
| Protocol Service Supported | This property, of type BACnetServicesSupported, indicates which standardized protocol services are executed by this device's protocol implementation. Penum_BACnetServicesSupported=ENUMERATION OF( ALARM AND EVENT SERVICES FILE ACCESS SERVICES OBJECT ACCESS SERVICES REMOTE DEVICE MANAGEMENT SERVICES VIRTUAL TERMINAL SERVICES REMOVED SERVICES UNCOMFIRMED SERVICES SERVICE ADDED AFTER 1995 SERVICE ADDED AFTER 2012) | Pset_BACnetDeviceObject.ProtocolServiceSupported ->IfcLabel::PEnum_BACnetServicesSupported | √ |  |  | PropertySets for Objects
| Protocol Object Type Supported | PEnum_BACnetObjectTypeSupported=ENUMERATION OF( all 60 BACnet objects types) | Pset_BACnetDeviceObject.SystemStatus ->IfcLabel::PEnum_BACnetObjectTypesSupported |  |  |  | PropertySets for Objects
| Object List | This read-only property is a BACnetARRAY of BACnetObjectIdentifier, one Object_Identifier for each object within the device that is accessible through BACnet services. | IfcObjectDefinition.IsdecomposedBy->IfcRelAggregates | √ |  |  | Object Definition Decomposition
| Max APDU Length Accepted | This property, of type Unsigned, is the maximum number of octets that may be contained in a single, indivisible application layer protocol data unit. | Pset_BACnetDeviceObject.MaxAPDULengthAccepted ->IfcReal | √ |  |  | PropertySets for Objects
| Segmentation Supported | This property, of type BACnetSegmentation, indicates whether the BACnet device supports segmentation of messages and, if so, whether it supports segmented transmission, reception, or both: PEnum_BACnetSegmentation = ENUMERATION OF(SEGMENTED_BOTH, SEGMENTED_TRANSMIT, SEGMENTED_RECEIVE, NO_SEGMENTATION) | Pset_BACnetDeviceObject.SegmentationSupported ->IfcLabel::PEnum_BACnetSegmentation | √ |  |  | PropertySets for Objects
| APDU Timeout | The APDU_Timeout property, of type Unsigned, shall indicate the amount of time in milliseconds between retransmissions of an APDU requiring acknowledgment for which no acknowledgment has been received. | Pset_BACnetDeviceObject.APDUTimeout ->IfcTimeMeasure | √ |  |  | PropertySets for Objects
| Number of APDU Retries | The Number_Of_APDU_Retries property, of type Unsigned, shall indicate the maximum number of times that an APDU shall be retransmitted. A suggested default value for this property is 3. | Pset_BACnetDeviceObject.NumberOfAPDURetries ->IfcInteger | √ |  |  | PropertySets for Objects
| Device Address Binding | The Device_Address_Binding property is a BACnetLIST of BACnetAddressBinding each of which consists of a BACnet Object_Identifier of a Device object and a BACnet device address in the form of a BACnetAddress. | Pset_BACnetDeviceObject.DeviceAddressBinding ->IfcPostalAddress | √ |  |  | PropertySets for Objects
| Database Revision | This property, of type Unsigned, is a logical revision number for the device's database | Pset_BACnetDeviceObject.DatabaseRevision ->IfcInteger | √ |  |  | PropertySets for Objects
| Property List |  | IfcPropertySet | √ |  |  | PropertySets for Objects
| Tags |  | IfcElement.Tag->IfcIdentifier |  |  | √ | Element Occurrence Attributes
BACnet Event Enrollment Object Type |  |  | IfcEvent assigned to IfcCotroller
| Has Assignment |  | IfcEvent.HasAssignment->IfcRelAssignsToControl |  |  |  | BACnet-Event Assign to Controller
| Decomposes | which device is the object decomposed by | IfcObjectDefinition.Decomposes->IfcRelAggregates |  |  | √ | Object Definition Composition
| Object Identifier |  | IfcRoot.GlobalId->IfcGloballyUniqueId | √ |  |  | Software Identity
| Object Name |  | IfcRoot.Name->IfcLable | √ |  |  | Object User Identity
| Object Type | IfcEvent assigned to IfcCotroller | IfcProcedure.PredefinedType->IfcProcedureTypeEnum | √ |  |  | BACnet Procedure Predefined Type; Object Predefined Type
| Event Type | This read-only property, of type BACnetEventType, indicates the type of event algorithm that is to be used to detect the occurrence of events and the event value notification parameters conveyed in event notifications. The value of this property is an enumerated type that may have any standard BACnetEventType value except CHANGE_OF_RELIABILITY. PEnum_BACnetEventType= ENUMERATION OF(NONE, ACCESS EVENT, BUFFER READY, CHANGE OF BITSTRING, CHANGE OF CHARACTERSTRING, CHANGE OF DISCRETE VALUE, CHANGE OF LIFE SAFETY, CHANGE OF STATE, CHANGE OF STATUS FLAGS, CHANGE OF TIMER, CHANGE OF VALUE, COMMAND FAILURE, DOUBLE OUT OF RANGE, EXTENDED, FLOATING LIMIT, OUT OF RANGE, SIGNED OUT OF RANGE, UNSIGNED OUT OF RANGE) | Pset_BACnetEventEnrollmentObject.EventType ->IfcLabel::PEnum_BACnetEventType | √ |  |  | PropertySets for Objects
| Notify Type | This property, of type BACnetNotifyType, shall convey whether the notifications generated by the object should be Events or Alarms. The value of the property is used as the value of the 'Notify Type' service parameter in event notifications generated by the object. PEnum_BACnetNotifyType=ENUMERATION OF (ALARM, EVENT, ACK-NOTIFICATION) | Pset_BACnetEventEnrollmentObject.NotifyType ->IfcLabel::PEnum_BACnetNotifyType | √ |  |  | PropertySets for Objects
| Event Parameters | The Event_Parameters property, of type BACnetEventParameter, determines the algorithm used to monitor the referenced object and provides the parameter values needed for this event algorithm. The parameter values specified in this property serve as event algorithm parameters and as reference type parameters reference properties whose values are used as event algorithm parameters, as defined by the respective event algorithm in Clause 13.3. PEnum_BACnetEventParameter=ENUMERATION OF (CHANGE OF BITSTRING, CHANGE OF STATE, CHANGE OF VALUE, COMMAND FAILURE, FLOATING LIMIT, OUT OF RANGE, CHANGE OF LIFE SAFETY, EXTENDED, BUFFER READY, UNSIGNED RANGE, ACCESS EVENT, DOUBLE OUT OF RANGE, SIGNED OUT OF RANGE, CHANGE OF CHARACTERSTRING, CHANGE OF STATUS FLAGS, NONE, CHANGE OF DISCRETE VALUE, CHANGE OF TIMER) | Pset_BACnetEventEnrollmentObject.EventParameters ->IfcLabel:: PEnum_BACnetEventParameter | √ |  |  | PropertySets for Objects
| Object Property Reference | This property, of type BACnetDeviceObjectPropertyReference, designates the particular object and property referenced by this Event Enrollment object. PEnum_BACnetDeviceObjectPropertyReference,=ENUMERATION OF( OBJECT IDENTIFIER, PROPERTY IDENTIFIER, PROPERTY ARRAY INDEX, DEVICE IDENTIFIER) | Pset_BACnetEventEnrollmentObject.ObjectPropertyReference ->IfcLabel:: BACnetDeviceObjectPropertyReference | √ |  |  | PropertySets for Objects
| Event State | PEnum_BACnetEventState = ENUMERATION OF( NORMAL, OFFNORMAL, FAULT); | Pset_BACnetEventEnrollmentObject.EventState ->IfcLabel:: PEnum_BACnetEventState | √ |  |  | PropertySets for Objects
| Event Enable | This property, of type BACnetEventTransitionBits, shall convey three flags that separately enable and disable the distribution of TO_OFFNORMAL, TO_FAULT, and TO_NORMAL notifications PEnum_BACnetEventTransitionBits = ENUMERATION OF( TO OFFNORMAL, TO FAULT TO NORMAL); | Pset_BACnetEventEnrollmentObject.EventEnable ->IfcLabel:: PEnum_BACnetEventTransitionBits | √ |  |  | PropertySets for Objects
| Acked Transitions | This read-only property, of type BACnetEventTransitionBits, shall convey three flags that separately indicate the acknowledgment state for TO_OFFNORMAL, TO_FAULT, and TO_NORMAL events (see Clause 13.2.2.1.5). Each flag shall have the value TRUE if no event of that type has ever occurred for the object. | Pset_BACnetEventEnrollmentObject.AckedTransitions ->IfcLabel:: PEnum_BACnetEventTransitionBits | √ |  |  | PropertySets for Objects
| Notification Class | This property, of type Unsigned, shall specify the instance of the Notification Class object to use for event-notificationdistribution. Notification class Object Type mappped to IfcProcedure | IfcProcedure.PredefinedType->IfcProcedureTypeEnum | √ |  |  | BACnet Procedure Assign to Event
| Event Time Stamps | This read-only property, of type BACnetARRAY[3] of BACnetTimeStamp, shall convey the times of the last TO_OFFNORMAL, TO_FAULT, and TO_NORMAL events (see Clause 13.2.2.1). Timestamps of type Time or Date shall have X'FF' in each octet, and Sequence Number timestamps shall have the value 0 if no event of that type has ever occurred for the object. PEnum_BACnetTimeStamp = ENUMERATION OF( TIME, SEQUENCE NUMBER DATETIME); | Pset_BACnetEventEnrollmentObject.EventTimeStamps ->IfcLabel:: PEnum_BACnetTimeStamp | √ |  |  | PropertySets for Objects
| Event Detection Enable | This property, of type BOOLEAN, indicates whether (TRUE) or not (FALSE) intrinsic reporting is enabled in the object and controls whether (TRUE) or not (FALSE) the object will be considered by event summarization services. | Pset_BACnetEventEnrollmentObject.EventDetectionEnable ->IfcBoolean | √ |  |  | PropertySets for Objects
| Status Flags | PEnum_BACnetStatusFlags = ENUMERATION OF( IN_ALARM, FAULT, OVERRIDEN, OUT_OF_SERVICE); | Pset_BACnetEventEnrollmentObject.StatusFlags ->IfcLabel:: PEnum_BACnetStatusFlag | √ |  |  | PropertySets for Objects
| Reliability | This property, of type BACnetReliability, provides an indication of the reliability of the Event Enrollment object to perform its monitoring function in addition to the reliability of the monitored object. PEnum_BACnetReliability = ENUMERATION OF( NO FAULT DETECTED, NO SENSOR, OVER RANGE, UNDER RANGE, OPEN LOOP, SHORTED LOOP, NO OUTPUT, UNRELIABLE OTHER, PROCESS ERROR, MULTI STATE FAULT, CONFIGURATION ERROR, COMMUNIVATION FAILURE, MEMBER FAULT, MONITORED OBJECT FAULT, TRIPPED, LAMP FAILURE, ACTIVATION FAILURE, RENEW DHCP FAILURE, RENEW DF REGISTRATION FAILURE, RESTART FAILURE, PROPRIETARY COMMAND FAILURE, FAULTS LISTED REFERENCE OBJECT FAULT); | Pset_BACnetEventEnrollmentObject.Reliability ->IfcLabel:: PEnum_BACnetReliability | √ |  |  | PropertySets for Objects
| Property List |  | IfcPropertySet | √ |  |  | PropertySets for Objects
BACnet File Object Type |  |  | IfcProxy
| Association | IfcProxy having associated file using IfcRelAssociatesDocument and IfcDocumentInformation | IfcObjectDefinition.HasAssociation->IfcRelAssociatesDocument | √ |  |  | Document Association
| Decomposes | which device is the object decomposed by | IfcObjectDefinition.Decomposes->IfcRelAggregates |  | √ |  | Object Definition Composition
| Object Identifier |  | IfcRoot.GlobalId->IfcGloballyUniqueId | √ |  |  | Software Identity
| Object Name |  | IfcRoot.Name->IfcLable | √ |  |  | Object User Identity
| Object Type | IfcProxy assigned to IfcCotroller | IfcObject.ObjectType->IfcLabel | √ |  |  | Object Predefined Type
| File Type | This property, of type CharacterString, identifies the intended use of this file. | IfcDocumentReference.Description->IfcText | √ |  |  | Document Association
| File Size | This property, of type Unsigned, indicates the size of the file data in octets. If the size of the file can be changed by writing to the file, and File_Access_Method is STREAM_ACCESS, then this property shall be writable. | Pset_BACnetFileObject.FileSize ->IfcReal | √ |  |  | PropertySets for Objects
| Modification Date | This property, of type BACnetDateTime, indicates the last time this object's underlying file data or File_Size was modified. | Pset_BACnetFileObject.ModificationDate->IfcDateTime | √ |  |  | PropertySets for Objects
| Read Only | This property, of type BOOLEAN, indicates whether (FALSE) or not (TRUE) the file data may be changed through the use of a BACnet AtomicWriteFile service. | Pset_BACnetFileObject.ReadOnly->IfcBoolean | √ |  |  | PropertySets for Objects
| File Access Method | This property, of type BACnetFileAccessMethod, indicates the type(s) of file access supported for this object. The possible values for File_Access_Method are: {RECORD_ACCESS, STREAM_ACCESS} | Pset_BACnetFileObject.FileAccessMethod ->IfcLabel:: PEnum_BACnetFileAccessMethod | √ |  |  | PropertySets for Objects
| Property List |  | IfcPropertySet | √ |  |  | PropertySets for Objects
BACnet Group Object Type |  |  | IfcDistributionSystem |  |  |  |  | no custon pset
| Object Identifier |  | IfcRoot.GlobalId->IfcGloballyUniqueId | √ |  |  | Software Identity
| Object Name |  | IfcRoot.Name->IfcLable | √ |  |  | Object User Identity
| Object Type | having predefined type=CONTROL | IfcDistrubutionSystem.PredefinedType ->IfcDistributionSystemEnum | √ |  |  | BACnet Distribution system Predefined Type; Object Predefined Type
| List Of Group Members | This property, of type BACnetLIST of ReadAccessSpecification, is a list of one or more read access specifications, which defines the members of the group that shall be referenced when this object is specified in a protocol transaction. | IfcDistrubutionSystem.Decomposes ->IfcRelAggregates | √ |  |  | Object Definition Composition
| Present Value | This property, of type BACnetLIST of ReadAccessResult, is a list that contains the values of all the properties specified in the List_Of_Group_Members. This is a "read-only" property; it cannot be used to write a set of values to the members of the group. The Present_Value list shall be reconstructed each time the property is read by fetching the member properties. (NOTE: This requirement is to reduce concurrency problems that could result if the Present_Value were stored.) | IfcDistributionSystem.IsDefinedBy->IfcRelDefinesByProperties | √ |  |  | PropertySets for Objects
| Property List |  | IfcPropertySet |  |  |  | PropertySets for Objects
BACnet Life Safety Point Object Type |  |  | IfcSensor, predefined Type=FIRESENSOR
| Object Geometric Representation | Geometric representation of the object | IfcProduct.Representation->IfcProductDefinitionShape |  | √ |  | Box Geometry; FootPrint Annotation Geometry
| Object Placement | placement of the object | IfcProduct.ObjectPlacement->IfcObjectPlacement |  | √ |  | Product local placement
| Object Contained in Space | the object contained in space | IfcElement.ContainedInStructure ->IfcRelContainedInSpatialStructure |  | √ |  | Spatial Containment
| Object Connected From | other objects connection | IfcElement.ConnectedFrom->IfcRelConnectsElements |  | √ |  | Path Connectivity
| Decomposes | which device is the object decomposed by | IfcObjectDefinition.Decomposes->IfcRelAggregates |  | √ |  | Object Definition Composition
| Object Identifier |  | IfcRoot.GlobalId->IfcGloballyUniqueId | √ |  |  | Software Identity
| Object Name |  | IfcRoot.Name->IfcLable | √ |  |  | Object User Identity
| Object Type | having predefined type=FIRESENSOR | IfcDistrubutionSystem.PredefinedType ->IfcDistributionSystemEnum | √ |  |  | BACnet sensor Predefined Type; Object Predefined Type
| Present Value | This property, of type BACnetLifeSafetyState, reflects the state of the Life Safety Point object. PEnum_BACnetLifeSafetyState=ENUMERATION OF( QUIET, PRE-ALARM, ALARM, FAULT, FAULT-PRE-ALARM,NOT-READY, ACTIVE, TAMPER, TEST-ALARM, TEST-ACTIVE, TEST-FAULT, TEST-FAULT-ALARM, HOLDUP, DURESS, TAMPER-ALARM, ABNORMAL, EMERGENCY-POWER, DELAYED,BLOACKED, LOCAL-ALARM, GENERAL-ALARM, SUPERVISORY, TEST-SUPERVISORY} | Pset_BACnetLifeSafetyPointObject.PresentValue ->IfcLabel:: PEnum_BACnetLifeSafetyState | √ |  |  | PropertySets for Objects
| Tracking Value | This property, of type BACnetLifeSafetyState, reflects the non-latched state of the Life Safety Point object. | Pset_BACnetLifeSafetyPointObject.TrackingValue ->IfcLabel:: PEnum_BACnetLifeSafetyState | √ |  |  | PropertySets for Objects
| Status Flags | PEnum_BACnetStatusFlags = ENUMERATION OF( IN_ALARM, FAULT, OVERRIDEN, OUT_OF_SERVICE); | Pset_BACnetLifeSafetyPointObject.StatusFlags ->IfcLabel:: PEnum_BACnetStatusFlag | √ |  |  | PropertySets for Objects
| Event State | PEnum_BACnetEventState = ENUMERATION OF( NORMAL, OFFNORMAL, FAULT); | Pset_BACnetLifeSafetyPointObject.EventState ->IfcLabel:: PEnum_BACnetEventState | √ |  |  | PropertySets for Objects
| Out of Service | The Out_Of_Service property, of type BOOLEAN, is an indication whether (TRUE) or not (FALSE) the input(s) or process the object represents is not in service. | Pset_BACnetLifeSafetyPointObject.OutOfService ->IfcBoolean | √ | ` |  | PropertySets for Objects
| Reliability | The Reliability property, of type BACnetReliability, provides an indication of whether the Present_Value or the operation of the physical input(s) in question are "reliable" as far as the BACnet device or operator can determine and, if not, why. | Pset_BACnetLifeSafetyPointObject.Reliability ->IfcLabel:: PEnum_BACnetReliability | √ |  |  | PropertySets for Objects
| Accepted Modes | This read-only property, of type BACnetLIST of BACnetLifeSafetyMode, shall specify all values the Mode property accepts when written to using BACnet services. PEnum_BACnetLifeSafetyMode=ENUMERATION OF( OFF, ON, TEST, MANNED, UNMANNED, ARMED, DISARMED, PREARMED, SLOW, FAST, DISCONNECTED, ENABLED, DISABLED, AUTOMATICE-RELEASE-DISABLED, DEFAULT) | Pset_BACnetLifeSafetyPointObject.AcceptedModes ->IfcLabel:: PEnum_BACnetLifeSafetyMode | √ |  |  | PropertySets for Objects
| Silenced | This property, of type BACnetSilencedState, shall indicate whether the most recently occurring transition for this object that has produced an audible or visual indication has been silenced by the receipt of a LifeSafetyOperation service request or a local process. PEnum_BACnetSilencedState=EMUMERATION OF( UNSILENCED, AUDIBLE-SILENCED, VISIBLE-SILENCED, ALL-SILENCED) | Pset_BACnetLifeSafetyPointObject.Silenced ->IfcLabel:: PEnum_BACnetSilencedState | √ |  |  | PropertySets for Objects
| Opreation Expected | The Operation_Expected property, of type BACnetLifeSafetyOperation, shall specify the next operation expected by this object to handle a specific life safety situation. PEnum_BACnetLifeSafetyOperation=ENUMERATION OF( NONE, SILENCE, SILENCE-AUDIBLE, SILENCE-VISUAL,RESET, RESET-ALARM,.RESET-FAULT, UNSILENCE, UNSILENCE-AUDIBLE, UNSILENCE-VISUAL) | Pset_BACnetLifeSafetyPointObject.OperationExpected ->IfcLabel:: PEnum_BACnetLifeSafetyOperationy | √ |  |  | PropertySets for Objects
| Property List |  | IfcPropertyList | √ |  |  | PropertySets for Objects
BACnet Life Safety Zone Object Type |  |  | IfcZone, predefined Type=FIRESAFETY
| Object Contained in Space | the object contained in space | IfcElement.ContainedInStructure ->IfcRelContainedInSpatialStructure |  | √ |  | Spatial Structure
| Decomposes | which device is the object decomposed by | IfcObjectDefinition.Decomposes->IfcRelAggregates |  | √ |  | Object Definition Composition
| Object Identifier |  | IfcRoot.GlobalId->IfcGloballyUniqueId | √ |  |  | Software Identity
| Object Name |  | IfcRoot.Name->IfcLable | √ |  |  | Object User Identity
| Object Type | having predefined type=FIREZONE | IfcDistrubutionSystem.PredefinedType ->IfcDistributionSystemEnum | √ |  |  | Object Predefined Type
| Present Value | This property, of type BACnetLifeSafetyState, reflects the state of the Life Safety Point object. PEnum_BACnetLifeSafetyState=ENUMERATION OF( QUIET, PRE-ALARM, ALARM, FAULT, FAULT-PRE-ALARM,NOT-READY, ACTIVE, TAMPER, TEST-ALARM, TEST-ACTIVE, TEST-FAULT, TEST-FAULT-ALARM, HOLDUP, DURESS, TAMPER-ALARM, ABNORMAL, EMERGENCY-POWER, DELAYED,BLOACKED, LOCAL-ALARM, GENERAL-ALARM, SUPERVISORY, TEST-SUPERVISORY} | Pset_BACnetLifeSafetyZoneObject.PresentValue ->IfcLabel:: PEnum_BACnetLifeSafetyState | √ |  |  | PropertySets for Objects
| Tracking Value | This property, of type BACnetLifeSafetyState, reflects the non-latched state of the Life Safety Point object. | Pset_BACnetLifeSafetyZoneObject.TrackingValue ->IfcLabel:: PEnum_BACnetLifeSafetyState | √ |  |  | PropertySets for Objects
| Status Flags | PEnum_BACnetStatusFlags = ENUMERATION OF( IN_ALARM, FAULT, OVERRIDEN, OUT_OF_SERVICE); | Pset_BACnetLifeSafetyZoneObject.StatusFlags ->IfcLabel:: PEnum_BACnetStatusFlag | √ |  |  | PropertySets for Objects
| Event State | PEnum_BACnetEventState = ENUMERATION OF( NORMAL, OFFNORMAL, FAULT); | Pset_BACnetLifeSafetyZoneObject.EventState ->IfcLabel:: PEnum_BACnetEventState | √ |  |  | PropertySets for Objects
| Out of Service | The Out_Of_Service property, of type BOOLEAN, is an indication whether (TRUE) or not (FALSE) the input(s) or process the object represents is not in service. | Pset_BACnetLifeSafetyZoneObject.OutOfService ->IfcBoolean | √ | ` |  | PropertySets for Objects
| Reliability | The Reliability property, of type BACnetReliability, provides an indication of whether the Present_Value or the operation of the physical input(s) in question are "reliable" as far as the BACnet device or operator can determine and, if not, why. | Pset_BACnetLifeSafetyZoneObject.Reliability ->IfcLabel:: PEnum_BACnetReliability | √ |  |  | PropertySets for Objects
| Accepted Modes | This read-only property, of type BACnetLIST of BACnetLifeSafetyMode, shall specify all values the Mode property accepts when written to using BACnet services. PEnum_BACnetLifeSafetyMode=ENUMERATION OF( OFF, ON, TEST, MANNED, UNMANNED, ARMED, DISARMED, PREARMED, SLOW, FAST, DISCONNECTED, ENABLED, DISABLED, AUTOMATICE-RELEASE-DISABLED, DEFAULT) | Pset_BACnetLifeSafetyZoneObject.AcceptedModes ->IfcLabel:: PEnum_BACnetLifeSafetyMode | √ |  |  | PropertySets for Objects
| Silenced | This property, of type BACnetSilencedState, shall indicate whether the most recently occurring transition for this object that has produced an audible or visual indication has been silenced by the receipt of a LifeSafetyOperation service request or a local process. PEnum_BACnetSilencedState=EMUMERATION OF( UNSILENCED, AUDIBLE-SILENCED, VISIBLE-SILENCED, ALL-SILENCED) | Pset_BACnetLifeSafetyZoneObject.Silenced ->IfcLabel:: PEnum_BACnetSilencedState | √ |  |  | PropertySets for Objects
| Opreation Expected | The Operation_Expected property, of type BACnetLifeSafetyOperation, shall specify the next operation expected by this object to handle a specific life safety situation. PEnum_BACnetLifeSafetyOperation=ENUMERATION OF( NONE, SILENCE, SILENCE-AUDIBLE, SILENCE-VISUAL,RESET, RESET-ALARM,.RESET-FAULT, UNSILENCE, UNSILENCE-AUDIBLE, UNSILENCE-VISUAL) | Pset_BACnetLifeSafetyZoneObject.OperationExpected ->IfcLabel:: PEnum_BACnetLifeSafetyOperation | √ |  |  | PropertySets for Objects
| Zone Members | This property, of type BACnetLIST of BACnetDeviceObjectReference, shall indicate which Life Safety Point and Life Safety Zone objects are members of the zone represented by this object. | IfcObjectDefinition.Nests->IfcObject |  |  |  | Object Nesting
| Property List |  | IfcPropertyList | √ |  |  | PropertySets for Objects
BACnet Loop Object Type |  |  | IfcController, predefined type=PROPORTIONAL
| Object Geometric Representation | Geometric representation of the object | IfcProduct.Representation->IfcProductDefinitionShape |  | √ |  | Box Geometry; FootPrint Annotation Geometry
| Object Placement | placement of the object | IfcProduct.ObjectPlacement->IfcObjectPlacement |  | √ |  | Product local placement
| Object Contained in Space | the object contained in space | IfcElement.ContainedInStructure ->IfcRelContainedInSpatialStructure |  | √ |  | Spatial Containment
| Object Connected From | other objects connection | IfcElement.ConnectedFrom->IfcRelConnectsElements |  | √ |  | Path Connectivity
| Decomposes | which device is the object decomposed by | IfcObjectDefinition.Decomposes->IfcRelAggregates |  | √ |  | Object Definition Composition
| Object Identifier | This property, of type BACnetObjectIdentifier, is a numeric code that is used to identify the object. It shall be unique within the BACnect device that maintains it | IfcControllort.GlobalId->IfcGloballyUniqueId | √ |  |  | Software Identity
| Object Name | This property, of type CharacterString, shall represent a name for the object that is unique within the BACnet device that maintains it. The minimum length of the string shall be one character. The set of characters used in the Object_Name shall be restricted to printable characters | IfcControllor.Name->IfcLable | √ |  |  | Object User Identity
| Object Type | Predefined Type =PROPORTIONAL | IfcController.PredefinedType->IfcControllerTypeEnum | √ |  |  | BACnet Controllor Predefined Type; Object Predefined Type
| Present Value | This property, of type REAL, indicates the current value, in engineering units, of the input being measured. ThePresent_Value property shall be writable when Out_Of_Service is TRUE | Pset_ControllerTypeProportional.Value->IfcReal | √ |  |  | PropertySets for Objects
| Status Flags | This property, of type BACnetStatusFlags, represents four Boolean flags that indicate the general “health” of object. PEnum_BACnetStatusFlagsEnum = ENUMERATION OF( IN_ALARM, FAULT, OVERRIDEN, OUT_OF_SERVICE); | Pset_BACnetLoopObject.StatusFlags ->IfcLabel:: PEnum_BACnetStatusFlag | √ |  |  | PropertySets for Objects
| Event State | The Event_State property, of type BACnetEventState, is included in order to provide a way to determine whether this object has an active event state associated with it. PEnum_BACnetEventStateEnum = ENUMERATION OF( NORMAL, OFFNORMAL, FAULT); | Pset_BACnetLoopObject.EventState ->IfcLabel:: PEnum_BACnetEventState | √ |  |  | PropertySets for Objects
| Reliability | The Reliability property, of type BACnetReliability, provides an indication of whether the Present_Value or the operation of the physical input(s) in question are "reliable" as far as the BACnet device or operator can determine and, if not, why. | Pset_BACnetLoopObject.Reliability ->IfcLabel:: PEnum_BACnetReliability | √ |  |  | PropertySets for Objects
| Out of Service | The Out_Of_Service property, of type BOOLEAN, is an indication whether (TRUE) or not (FALSE) the physical input that the object represents is not in service. | Pset_BACnetLoopObject.OutOfService ->IfcBoolean | √ | ` |  | PropertySets for Objects
| Output Units | This property, of type BACnetEngineeringUnits, indicates the engineering units for the output (Present_Value property) of this control loop. | Pset_BACnetLoopObject.OutputUnits ->IfcLabel | √ |  |  | PropertySets for Objects
| Manipulated Variable reference | This property is of type BACnetObjectPropertyReference. The output (Present_Value) of the control loop is written to the object and property designated by the Manipulated_Variable_Reference. It is normally the Present_Value of an Analog Output object used to position a device, but it could also be another object or property, such as that used to stage multiple Binary Outputs. | IfcProduct.ReferencedBy ->IfcRelAssignsToProduct.RelatedObject->IfcObject IfcObject.IsDefinedBy->IfcRelDefinesByProperties.RelatedPropertyDefinition -> IfcPropertySet | √ |  |  | Produce assignment and Property Sets for Objects
| Controlled Variable reference | This property is of type BACnetObjectPropertyReference. | IfcProduct.ReferencedBy ->IfcRelAssignsToProduct.RelatedObject->IfcObject IfcObject.IsDefinedBy->IfcRelDefinesByProperties.RelatedPropertyDefinition -> IfcPropertySet | √ |  |  | Produce assignment and Property Sets for Objects
| Controlled Variable Value | This property, of type REAL, is the value of the property of the object referenced by the Controlled_Variable_Reference property. | IfcProduct.ReferencedBy ->IfcRelAssignsToProduct.RelatedObject->IfcObject IfcObject.IsDefinedBy->IfcRelDefinesByProperties.RelatedPropertyDefinition -> IfcPropertySet | √ |  |  | Produce assignment and Property Sets for Objects
| Controlled Variable Units | This property, of type BACnetEngineeringUnits, indicates the engineering units for the Controlled_Variable_Value property of this object. | IfcProduct.ReferencedBy ->IfcRelAssignsToProduct.RelatedObject->IfcObject IfcObject.IsDefinedBy->IfcRelDefinesByProperties.RelatedPropertyDefinition -> IfcPropertySet | √ |  |  | Produce assignment and Property Sets for Objects
| Setpoint reference | This property, of type BACnetSetpointReference, contains zero or one references. | IfcProduct.ReferencedBy ->IfcRelAssignsToProduct.RelatedObject->IfcObject IfcObject.IsDefinedBy->IfcRelDefinesByProperties.RelatedPropertyDefinition -> IfcPropertySet | √ |  |  | Produce assignment and Property Sets for Objects
| Setpoint | This property, of type REAL, is the value of the loop setpoint or of the property of the object referenced by the Setpoint_Reference, expressed in units of the Controlled_Variable_Units property. | IfcProduct.ReferencedBy ->IfcRelAssignsToProduct.RelatedObject->IfcObject IfcObject.IsDefinedBy->IfcRelDefinesByProperties.RelatedPropertyDefinition -> IfcPropertySet | √ |  |  | Produce assignment and Property Sets for Objects
| Action | This property, of type BACnetAction, defines whether the loop is DIRECT or REVERSE acting. | Pset_BACnetLoopObject.Action ->IfcLabel::Penum_BACnetAction | √ |  |  | PropertySets for Objects
| Property List | This read-only property is a BACnetARRAY of property identifiers, one property identifier for each property that exists within the object. | IfcPropertySet.HasPropertites->IfcProperty | √ |  |  | PropertySets for Objects
BACnet Multi-state Input Object Type |  |  | IfcController, predefined type=MULTIPOSITION
| Object Geometric Representation | Geometric representation of the object | IfcProduct.Representation->IfcProductDefinitionShape |  | √ |  | Box Geometry; FootPrint Annotation Geometry
| Object Placement | placement of the object | IfcProduct.ObjectPlacement->IfcObjectPlacement |  | √ |  | Product local placement
| Object Contained in Space | the object contained in space | IfcElement.ContainedInStructure ->IfcRelContainedInSpatialStructure |  | √ |  | Spatial Containment
| Object Connected From | other objects connection | IfcElement.ConnectedFrom->IfcRelConnectsElements |  | √ |  | Path Connectivity
| Decomposes | which device is the object decomposed by | IfcObjectDefinition.Decomposes->IfcRelAggregates |  | √ |  | Object Definition Composition
| Object Identifier | This property, of type BACnetObjectIdentifier, is a numeric code that is used to identify the object. It shall be unique within the BACnect device that maintains it | IfcControllort.GlobalId->IfcGloballyUniqueId | √ |  |  | Software Identity
| Object Name | This property, of type CharacterString, shall represent a name for the object that is unique within the BACnet device that maintains it. The minimum length of the string shall be one character. The set of characters used in the Object_Name shall be restricted to printable characters | IfcControllor.Name->IfcLable | √ |  |  | Object User Identity
| Object Type | Predefined Type =MULTIPOSITION | IfcController.PredefinedType->IfcControllerTypeEnum | √ |  |  | BACnet Controllor Predefined Type; Object Predefined Type
| Present Value | This property, of type Unsigned, reflects the logical state of the input.The logical state of the input shall be one of 'n' states, where 'n' is the number of states defined in the Number_Of_States property. | Pset_BACnetMultistateInputObject.PresentValue->IfcLabel | √ |  |  | PropertySets for Objects
| Status Flags | This property, of type BACnetStatusFlags, represents four Boolean flags that indicate the general “health” of object. PEnum_BACnetStatusFlagsEnum = ENUMERATION OF( IN_ALARM, FAULT, OVERRIDEN, OUT_OF_SERVICE); | Pset_BACnetMultistateInputObject.StatusFlags ->IfcLabel:: PEnum_BACnetStatusFlag | √ |  |  | PropertySets for Objects
| Event State | The Event_State property, of type BACnetEventState, is included in order to provide a way to determine whether this object has an active event state associated with it. PEnum_BACnetEventStateEnum = ENUMERATION OF( NORMAL, OFFNORMAL, FAULT); | Pset_BACnetMultistateInputObject.EventState ->IfcLabel:: PEnum_BACnetEventState | √ |  |  | PropertySets for Objects
| Out of Service | The Out_Of_Service property, of type BOOLEAN, is an indication whether (TRUE) or not (FALSE) the physical input that the object represents is not in service. | Pset_BACnetMultistateInputObject.OutOfService ->IfcBoolean | √ |  |  | PropertySets for Objects
| Number of States | This property, of type Unsigned, defines the number of states that the Present_Value may have. The Number_Of_States property shall always have a value greater than zero. | Pset_BACnetMultistateInputObject->IfcReal | √ |  |  | PropertySets for Objects
| Property List | This read-only property is a BACnetARRAY of property identifiers, one property identifier for each property that exists within the object. | IfcPropertySet.HasPropertites->IfcProperty | √ |  |  | PropertySets for Objects
BACnet Multi-state Input Object Type |  |  | IfcController, predefined type=MULTIPOSITION
| Object Geometric Representation | Geometric representation of the object | IfcProduct.Representation->IfcProductDefinitionShape |  | √ |  | Box Geometry; FootPrint Annotation Geometry
| Object Placement | placement of the object | IfcProduct.ObjectPlacement->IfcObjectPlacement |  | √ |  | Product local placement
| Object Contained in Space | the object contained in space | IfcElement.ContainedInStructure ->IfcRelContainedInSpatialStructure |  | √ |  | Spatial Containment
| Object Connected From | other objects connection | IfcElement.ConnectedFrom->IfcRelConnectsElements |  | √ |  | Path Connectivity
| Decomposes | which device is the object decomposed by | IfcObjectDefinition.Decomposes->IfcRelAggregates |  | √ |  | Object Definition Composition
| Object Identifier | This property, of type BACnetObjectIdentifier, is a numeric code that is used to identify the object. It shall be unique within the BACnect device that maintains it | IfcControllort.GlobalId->IfcGloballyUniqueId | √ |  |  | Software Identity
| Object Name | This property, of type CharacterString, shall represent a name for the object that is unique within the BACnet device that maintains it. The minimum length of the string shall be one character. The set of characters used in the Object_Name shall be restricted to printable characters | IfcControllor.Name->IfcLable | √ |  |  | Object User Identity
| Object Type | Predefined Type =MULTIPOSITION | IfcController.PredefinedType->IfcControllerTypeEnum | √ |  |  | BACnet Controllor Predefined Type; Object Predefined Type
| Status Flags | This property, of type BACnetStatusFlags, represents four Boolean flags that indicate the general “health” of object. PEnum_BACnetStatusFlagsEnum = ENUMERATION OF( IN_ALARM, FAULT, OVERRIDEN, OUT_OF_SERVICE); | Pset_BACnetMultistateInputObject.StatusFlags ->IfcLabel:: PEnum_BACnetStatusFlag | √ |  |  | PropertySets for Objects
| Event State | The Event_State property, of type BACnetEventState, is included in order to provide a way to determine whether this object has an active event state associated with it. PEnum_BACnetEventStateEnum = ENUMERATION OF( NORMAL, OFFNORMAL, FAULT); | Pset_BACnetMultistateInputObject.EventState ->IfcLabel:: PEnum_BACnetEventState | √ |  |  | PropertySets for Objects
| Out of Service | The Out_Of_Service property, of type BOOLEAN, is an indication whether (TRUE) or not (FALSE) the physical input that the object represents is not in service. | Pset_BACnetMultistateInputObject.OutOfService ->IfcBoolean | √ |  |  | PropertySets for Objects
| Number of States | This property, of type Unsigned, defines the number of states that the Present_Value may have. The Number_Of_States property shall always have a value greater than zero. | Pset_BACnetMultistateInputObject->IfcReal | √ |  |  | PropertySets for Objects
| Priority Array | array of BACnetPriorityValue::=CHOICE of (NULL,REAL,ENUMERATED,UNSIGNED, INTEGER, DOUBLE,TIME,CHARATERSTRING, OCETESTRING, BIT STRING, DATE, BACNETOBJECTIDENTIFIER, ABSTRACT-SYNTAX.&TYPE, BACNETDATETIME) | Pset_BACnetAnalogOutputObject.PriorityArray ->IfcLabel:: PEnum_BACnetPriorityValue | √ |  |  | PropertySets for Objects
| Relinquish Default | This property is the default value to be used for the Present_Value property when all command priority values in the Priority_Array property have a NULL value. | Pset_BACnetAnalogOutputObject.RelinquishDefault->IfcReal | √ |  |  | PropertySets for Objects
| Property List |  | IfcPropertySet.HasPropertites->IfcProperty | √ |  |  | PropertySets for Objects
| Current Command Priority | This read-only property, of type BACnetOptionalUnsigned, Indicates the currently active priority, The value of this property shall be equal to the index of the entry in the Priority_Array from which the Present_Value’s value has been taken. If Present_Value has taken on the value of Relinquish_Default, this property shall have the value Null. | Pset_BACnetAnalogOutputObject.CurrentCommandPriority->IfcInteger | √ |  |  | PropertySets for Objects
BACnet Multi-state Value Object Type |  |  | IfcController, predefined type=MULTIPOSITION
| Object Geometric Representation | Geometric representation of the object | IfcProduct.Representation->IfcProductDefinitionShape |  | √ |  | Box Geometry; FootPrint Annotation Geometry
| Object Placement | placement of the object | IfcProduct.ObjectPlacement->IfcObjectPlacement |  | √ |  | Product local placement
| Object Contained in Space | the object contained in space | IfcElement.ContainedInStructure ->IfcRelContainedInSpatialStructure |  | √ |  | Spatial Containment
| Object Connected From | other objects connection | IfcElement.ConnectedFrom->IfcRelConnectsElements |  | √ |  | Path Connectivity
| Decomposes | which device is the object decomposed by | IfcObjectDefinition.Decomposes->IfcRelAggregates |  | √ |  | Object Definition Composition
| Object Identifier | This property, of type BACnetObjectIdentifier, is a numeric code that is used to identify the object. It shall be unique within the BACnect device that maintains it | IfcControllort.GlobalId->IfcGloballyUniqueId | √ |  |  | Software Identity
| Object Name | This property, of type CharacterString, shall represent a name for the object that is unique within the BACnet device that maintains it. The minimum length of the string shall be one character. The set of characters used in the Object_Name shall be restricted to printable characters | IfcControllor.Name->IfcLable | √ |  |  | Object User Identity
| Object Type | Predefined Type =MULTIPOSITION | IfcController.PredefinedType->IfcControllerTypeEnum | √ |  |  | BACnet Controllor Predefined Type; Object Predefined Type
| Present Value | This property, of type Unsigned, reflects the logical state of the input.The logical state of the input shall be one of 'n' states, where 'n' is the number of states defined in the Number_Of_States property. | Pset_BACnetMultistateInputObject.PresentValue->IfcLabel | √ |  |  | PropertySets for Objects
| Status Flags | This property, of type BACnetStatusFlags, represents four Boolean flags that indicate the general “health” of object. PEnum_BACnetStatusFlagsEnum = ENUMERATION OF( IN_ALARM, FAULT, OVERRIDEN, OUT_OF_SERVICE); | Pset_BACnetMultistateInputObject.StatusFlags ->IfcLabel:: PEnum_BACnetStatusFlag | √ |  |  | PropertySets for Objects
| Event State | The Event_State property, of type BACnetEventState, is included in order to provide a way to determine whether this object has an active event state associated with it. PEnum_BACnetEventStateEnum = ENUMERATION OF( NORMAL, OFFNORMAL, FAULT); | Pset_BACnetMultistateInputObject.EventState ->IfcLabel:: PEnum_BACnetEventState | √ |  |  | PropertySets for Objects
| Out of Service | The Out_Of_Service property, of type BOOLEAN, is an indication whether (TRUE) or not (FALSE) the physical input that the object represents is not in service. | Pset_BACnetMultistateInputObject.OutOfService ->IfcBoolean | √ |  |  | PropertySets for Objects
| Number of States | This property, of type Unsigned, defines the number of states that the Present_Value may have. The Number_Of_States property shall always have a value greater than zero. | Pset_BACnetMultistateInputObject->IfcReal | √ |  |  | PropertySets for Objects
| Property List | This read-only property is a BACnetARRAY of property identifiers, one property identifier for each property that exists within the object. | IfcPropertySet.HasPropertites->IfcProperty | √ |  |  | PropertySets for Objects
BACnet Notification Class Object Type |  |  | IfcProcedure assigned to IfcControllor
| Has Assignment |  | IfcProcedure.HasAssignments ->IfcRelAssignsToControl.RelatedObjects ->IfcObject | √ |  |  | BACnet-Procedure Assign to Controller
| Decomposes | which device is the object decomposed by | IfcObjectDefinition.Decomposes->IfcRelAggregates |  | √ |  | Object Definition Composition
| Object Name |  | IfcRoot.Name->IfcLable | √ |  |  | Software Identity
| Object Idenfifier |  | IfcRoot.GlobalId->IfcGloballyUniqueId | √ |  |  | Object User Identity
| Object Type | IfcProcedure having PredefinedType=CALIBRATION, and assigned to IfcController having PredefinedType=NOTDEFINED | IfcProcedure.PredefinedType->IfcProcedureTypeEnum | √ |  |  | BACnet-Procedure Predefined Type; Object Predefined Type
| Notification Class | This property, of type Unsigned, shall specify the instance of the Notification Class object to use for event-notificationdistribution. | IfcProcedure.Name->IfcLabel | √ |  |  | Object User Identity
| Priority | This property, of type BACnetARRAY[3] of Unsigned, shall convey the priority to be used for event notifications for TO_OFFNORMAL, TO_FAULT, and TO_NORMAL events, respectively. | Pset_BACnetNotificationClassObject.Priority ->IfcLabel | √ |  |  | PropertySets for Objects
| Ack Required | This property, of type BACnetEventTransitionBits, shall convey three separate flags that represent whether acknowledgment shall be required in notifications generated for TO_OFFNORMAL, TO_FAULT, and TO_NORMAL event transitions | Pset_BACnetNotificationClassObject.AckRequired ->IfcLabel:: PEnum_BACnetEventTransitionBits | √ |  |  | PropertySets for Objects
| Recipient List | This property, of type BACnetLIST of BACnetDestination, shall convey a list of zero or more recipient destinations to which notifications shall be sent when event-initiating objects using this class detect the occurrence of an event. PEnum_BACnetDestination=ENUMERATION OF( VALID_DAYS, FROM_TIME, TO-TIME, RECIPIENT, PROCESS_IDENTIFIER, ISSUE_CONFIRMED_NOTIFICATIONS, TRANSITIONS) | Pset_BACnetNotificationClassObject.RecipientList ->IfcLabel:: PEnum_BACnetDestination | √ |  |  | PropertySets for Objects
| Property List | This read-only property is a BACnetARRAY of property identifiers, one property identifier for each property that exists within the object. | IfcPropertySet.HasPropertites->IfcProperty | √ |  |  | PropertySets for Objects
BACnet Program Object Type |  |  | IfcTask assigned to IfcControllor
| Has Assignment |  | IfcTask.HasAssignments ->IfcRelAssignsToControl.RelatedObjects ->IfcObject | √ |  |  | BACnet-Procedure Assign to Controller
| Decomposes | which device is the object decomposed by | IfcObjectDefinition.Decomposes->IfcRelAggregates |  | √ |  | Object Definition Composition
| Object Name |  | IfcRoot.Name->IfcLable | √ |  |  | Software Identity
| Object Idenfifier |  | IfcRoot.GlobalId->IfcGloballyUniqueId | √ |  |  | Object User Identity
| Object Type |  | IfcObject.ObjectType->IfcTLabel | √ |  |  | Object Predefined Type
| Program state | This property, of type BACnetProgramState, reflects the current logical state of the process executing the application program this object represents. This property is Read-Only. | Pset_BACnetProgramObject.ProgramState ->IfcLabel:: PEnum_BACnetProgramState | √ |  |  | PropertySets for Objects
| Status Flags | This property, of type BACnetStatusFlags, represents four Boolean flags that indicate the general “health” of object. PEnum_BACnetStatusFlagsEnum = ENUMERATION OF( IN_ALARM, FAULT, OVERRIDEN, OUT_OF_SERVICE); | Pset_BACnetProgramObject.StatusFlags ->IfcLabel:: PEnum_BACnetStatusFlag | √ |  |  | PropertySets for Objects
| Out of Service | The Out_Of_Service property, of type BOOLEAN, is an indication whether (TRUE) or not (FALSE) the physical input that the object represents is not in service. | Pset_BACnetProgramObject.OutOfService ->IfcBoolean | √ |  |  | PropertySets for Objects
| Property List | This read-only property is a BACnetARRAY of property identifiers, one property identifier for each property that exists within the object. | IfcPropertySet.HasPropertites->IfcProperty | √ |  |  | PropertySets for Objects
BACnet Pulse Converter Object Type |  |  | IfcController, predefined type=FLOATING
| Object Geometric Representation |  | IfcProduct.Representation->IfcProductDefinitionShape |  | √ |  | Box Geometry; FootPrint Annotation Geometry
| Object Placement |  | IfcProduct.ObjectPlacement->IfcObjectPlacement |  | √ |  | Product local placement
| Object Contained in Space | the object contained in space | IfcElement.ContainedInStructure ->IfcRelContainedInSpatialStructure |  | √ |  | Spatial Containment
| Object Connected From |  | IfcElement.ConnectedFrom->IfcRelConnectsElements |  | √ |  | Path Connectivity
| Decomposes | which device is the object decomposed by | IfcObjectDefinition.Decomposes->IfcRelAggregates |  | √ |  | Object Definition Composition
| Object Identifier |  | IfcRoot.GlobalId->IfcGloballyUniqueId | √ |  |  | Software Identity
| Object Name |  | IfcRoot.Name->IfcLable | √ |  |  | Object User Identity
| Object Type | Predefined Type =FLOATING | IfcController.PredefinedType->IfcControllerTypeEnum | √ |  |  | BACnet Controllor Predefined Type; Object Predefined Type
| Present Value | This property, of type REAL, indicates the accumulated value of the input being measured. It is computed by multiplying the current value of the Count property by the value of the Scale_Factor property. | Pset_ControllerTypeFloating.Value->IfcInteger | √ |  |  | PropertySets for Objects
| Status Flags | This property, of type BACnetStatusFlags, represents four Boolean flags that indicate the general “health” of object. PEnum_BACnetStatusFlagsEnum = ENUMERATION OF( IN_ALARM, FAULT, OVERRIDEN, OUT_OF_SERVICE); | Pset_BACnetMultistateInputObject.StatusFlags ->IfcLabel:: PEnum_BACnetStatusFlag | √ |  |  | PropertySets for Objects
| Event State | The Event_State property, of type BACnetEventState, is included in order to provide a way to determine whether this object has an active event state associated with it. PEnum_BACnetEventStateEnum = ENUMERATION OF( NORMAL, OFFNORMAL, FAULT); | Pset_BACnetPulseConverterObject.EventState ->IfcLabel:: PEnum_BACnetEventState | √ |  |  | PropertySets for Objects
| Out of Service | The Out_Of_Service property, of type BOOLEAN, is an indication whether (TRUE) or not (FALSE) the physical input that the object represents is not in service. | Pset_BACnetPulseConverterObject.OutOfService ->IfcBoolean | √ |  |  | PropertySets for Objects
| Units | This property, of type BACnetEngineeringUnits, indicates the measurement units of this object. | Pset_BACnetPulseConverterObject.Units ->IfcLabel | √ |  |  | PropertySets for Objects
| Scale Factor | This property, of type REAL, provides the conversion factor for computing Present_Value. | Pset_BACnetPulseConverterObject.ScaleFactor ->IfcReal | √ |  |  | PropertySets for Objects
| Count | This read-only property, of type Unsigned, indicates the count of the input pulses as acquired from the physical input or the property referenced by the Input_Reference property. | Pset_BACnetPulseConverterObject.ScaleFactor ->IfcInteger | √ |  |  | PropertySets for Objects
| Update Time | This read-only property, of type BACnetDateTime, reflects the date and time of the most recent change to the Count property as a result of input pulse accumulation and is updated atomically with the Count property. | Pset_BACnetPulseConverterObject.UpdateTime ->IfcDateTime | √ |  |  | PropertySets for Objects
| Count Change Time | This read-only property, of type BACnetDateTime, represents the date and time of the most recent occurrence of a write to the Adjust_Value property. | Pset_BACnetPulseConverterObject.CountChangeTime ->IfcDateTime | √ |  |  | PropertySets for Objects
| Count Before Change | This property, of type Unsigned, indicates the value of the Count property just prior to the most recent write to the Adjust_Value property. If no such write has yet occurred, this property shall have the value zero. | Pset_BACnetPulseConverterObject.CountBeforeChange ->IfcReal | √ |  |  | PropertySets for Objects
| Property List | This read-only property is a BACnetARRAY of property identifiers, one property identifier for each property that exists within the object. | IfcPropertySet.HasPropertites->IfcProperty | √ |  |  | PropertySets for Objects
BACnet Schedule Object Type |  |  | IfcPerformanceHistory, predefined type=OPERATION, IfcTimeSeries
| Decomposes | which device is the object decomposed by | IfcObjectDefinition.Decomposes->IfcRelAggregates |  | √ |  | Object Definition Composition
| Object Identifier |  | IfcRoot.GlobalId->IfcGloballyUniqueId | √ |  |  | Software Identity
| Object Name |  | IfcRoot.Name->IfcLable | √ |  |  | Object User Identity
| Object Type | Predefined Type =OPERATION | IfcPerformanceHistory.PredefinedType ->IfcPerformanceHistoryTypeEnum | √ |  |  | BACnet PerformanceHistory Predefined Type; Object Predefined Type
| Present Value | This property indicates the current value of the schedule, which may be any primitive datatype. | Pset_BACnetScheduleObject.PresentValue ->any | √ |  |  | PropertySets for Objects
| Effective Period | This property specifies the range of dates within which the Schedule object is active. | Pset_BACnetScheduleObject.EffectivePeriod ->P_BOUNDEDVALUE::IfcDateTime | √ |  |  | PropertySets for Objects
| Schedule Default | This property holds a default value to be used for the Present_Value property when no other scheduled value is in effect (see Clause 12.24.4). This may be any primitive datatype. | Pset_BACnetScheduleObject.ScheduleDefault ->any | √ |  |  | PropertySets for Objects
| List of Object Property References | This property specifies the Device Identifiers, Object Identifiers and Property Identifiers of the properties to be written with specific values at specific times on specific days. | IfcControl.Controls->IfcRelAssignsToControl.RelatedObjects->IfcObject IfcObject.IsDefinedBy->IfcRelDefinesByProperties.RelatedPropertyDefinition -> IfcPropertySet | √ |  |  | Control assignment and Property Sets for Objects
| Priority For Writing | This property defines the priority at which the referenced properties are commanded. It corresponds to the 'Priority' parameter of the WriteProperty service. It is an unsigned integer in the range 1-16, with 1 being considered the highest priority and 16 the lowest. | Pset_BACnetScheduleObject.PriorityForWriting ->P_BOUNDEDVALUE::IfcInteger | √ |  |  | PropertySets for Objects
| Status Flags | This property, of type BACnetStatusFlags, represents four Boolean flags that indicate the general “health” of object. PEnum_BACnetStatusFlagsEnum = ENUMERATION OF( IN_ALARM, FAULT, OVERRIDEN, OUT_OF_SERVICE); | Pset_BACnetScheduleObject.StatusFlags ->IfcLabel:: PEnum_BACnetStatusFlag | √ |  |  | PropertySets for Objects
| Event State | The Event_State property, of type BACnetEventState, is included in order to provide a way to determine whether this object has an active event state associated with it. PEnum_BACnetEventStateEnum = ENUMERATION OF( NORMAL, OFFNORMAL, FAULT); | Pset_BACnetScheduleObject.EventState ->IfcLabel:: PEnum_BACnetEventState | √ |  |  | PropertySets for Objects
| Reliability | The Reliability property, of type BACnetReliability, provides an indication of whether the Present_Value or the operation of the physical input(s) in question are "reliable" as far as the BACnet device or operator can determine and, if not, why. | Pset_BACnetScheduleObject.Reliability ->IfcLabel:: PEnum_BACnetReliability | √ |  |  | PropertySets for Objects
| Out of Service | The Out_Of_Service property, of type BOOLEAN, is an indication whether (TRUE) or not (FALSE) the physical input that the object represents is not in service. | Pset_BACnetScheduleObject.OutOfService ->IfcBoolean | √ |  |  | PropertySets for Objects
| Property List | This read-only property is a BACnetARRAY of property identifiers, one property identifier for each property that exists within the object. | IfcPropertySet.HasPropertites->IfcProperty | √ |  |  | PropertySets for Objects
BACnet Trend Log Object Type |  |  | IfcPerformanceHistory, predefined type=OPERATION, IfcTimeSeries
| Decomposes | which device is the object decomposed by | IfcObjectDefinition.Decomposes->IfcRelAggregates |  | √ |  | Object Definition Composition
| Object Identifier |  | IfcRoot.GlobalId->IfcGloballyUniqueId | √ |  |  | Software Identity
| Object Name |  | IfcRoot.Name->IfcLable | √ |  |  | Object User Identity
| Object Type | Predefined Type =OPERATION | IfcPerformanceHistory.PredefinedType ->IfcPerformanceHistoryTypeEnum | √ |  |  | BACnet PerformanceHistory Predefined Type; Object Predefined Type
| Stop When Full | This property, of type BOOLEAN, specifies whether (TRUE) or not (FALSE) logging should cease when the log buffer is full. | Pset_BACnetTrendLogObject.StopWhenFull ->IfcBoolean | √ |  |  | PropertySets for Objects
| Buffer Size | This property, of type Unsigned32, shall specify the maximum number of log records the log buffer may hold. | Pset_BACnetTrendLogObject.BufferSize ->IfcReal | √ |  |  | PropertySets for Objects
| Log Buffer | This property, of type BACnetLIST of BACnetLogRecord, is a list of up to Buffer_Size timestamped log records of datatype BACnetLogRecord, each of which conveys a recorded data value, an error related to data-collection, or status changes in the Trend Log object. PEnum_BACnetLogRecord=ENUMERATION OF( TIMESTAMP, LOG-DATUM, STATUS-FLAGS) | Pset_BACnetTrendLogObject.LogBuffer ->IfcLabel:: PEnum_BACnetLogRecord | √ |  |  | PropertySets for Objects
| Total Record Count | This property, of type Unsigned32, shall represent the total number of log records collected by the Trend Log object since creation | Pset_BACnetTrendLogObject.TotalRecordCount ->IfcReal | √ |  |  | PropertySets for Objects
| Logging Type | This property, of type BACnetLoggingType, specifies whether the Trend Log object collects log records using polling, COV or triggered acquisition. PEnum_BACnetLoggingType=ENUMERATION OF(POLLED, COV, TRIGGERED) | Pset_BACnetTrendLogObject.LoggingType ->IfcLabel:: PEnum_BACnetLoggingType | √ |  |  | PropertySets for Objects
| Status Flags | This property, of type BACnetStatusFlags, represents four Boolean flags that indicate the general “health” of object. PEnum_BACnetStatusFlagsEnum = ENUMERATION OF( IN_ALARM, FAULT, OVERRIDEN, OUT_OF_SERVICE); | Pset_BACnetScheduleObject.StatusFlags ->IfcLabel:: PEnum_BACnetStatusFlag | √ |  |  | PropertySets for Objects
| Event State | The Event_State property, of type BACnetEventState, is included in order to provide a way to determine whether this object has an active event state associated with it. PEnum_BACnetEventStateEnum = ENUMERATION OF( NORMAL, OFFNORMAL, FAULT); | Pset_BACnetScheduleObject.EventState ->IfcLabel:: PEnum_BACnetEventState | √ |  |  | PropertySets for Objects
| Property List | This read-only property is a BACnetARRAY of property identifiers, one property identifier for each property that exists within the object. | IfcPropertySet.HasPropertites->IfcProperty | √ |  |  | PropertySets for Objects
| 395 | [5 empty] | 362

## Sheet1
Property Set | Property Enumeration
Pset_BACnetAnalogInput Object | PEnum_BACnetAction
Pset_BACnetAnalogOutput Object | PEnum_BACnetDestination
Pset_BACnetAnalogValueObject | PEnum_BACnetDeviceObjectPropertyReference
Pset_BACnetAveragingObject | PEnum_BACnetDeviceStatus
Pset_BACnetBinaryInputObject | PEnum_BACnetEventParameter
Pset_BACnetBinaryOutputObject | PEnum_BACnetEventState
Pset_BACnetBinaryValueObject | PEnum_BACnetEventTimeStamp
Pset_BACnetCommandObject | PEnum_BACnetEventTrasitionStamp
Pset_BACnetDeviceObject | PEnum_BACnetEventTrasitionBits
Pset_BACnetEventEnrollmentObject | PEnum_BACnetEventType
Pset_BACnetFileObject | PEnum_BACnetFileAccessMethod
Pset_BACnetLifeSafetyPointObject | PEnum_BACnetLifeSafetyMode
Pset_BACnetLifeSafetyZoneObject | PEnum_BACnetLifeSafetyOperation
Pset_BACnetLoopObject | PEnum_BACnetLifeSafetyState
Pset_BACnetMulti-stateInputObject | PEnum_BACnetLoggingType
Pset_BACnetMulti-stateOutputObject | PEnum_BACnetLogRecord
Pset_BACnetMulti-stateValueObject | PEnum_BACnetNotifyType
Pset_BACnetNotificationClassObject | PEnum_BACnetPolarity
Pset_BACnetProgramObject | PEnum_BACnetPolarityArray
Pset_BACnetPulseConverterObject | PEnum_BACnetProgramState
Pset_BACnetScheduleObject | PEnum_BACnetReliability
Pset_BACnetTrendLogObject | PEnum_BACnetSegmentation
PEnum_BACnetServiceSupported
PEnum_BACnetSilencedState
PEnum_BACnetStatusFlag

## Sheet2
Exchange Requirement
Header Section
Name |  | ER_Exchange Final BAS Model
Identifier |  | BACnet_ER
Change Log
<2018-03-20> |  | Created BACnet objects and Properties | Stang93@gatech.edu
Project Stage | 31-10 00 00 | Inception Phase
| 31-20 00 00 | Conceptualization Phase
| 31-30 00 00 | Criteria Definition Phase
| 31-40 00 00 | Design Phase |  | √
| 31-50 00 00 | Coordination Phase |  | √
| 31-60 00 00 | Implementation Phase |  | √
| 31-70 00 00 | Handover Phase |  | √
| 31-80 00 00 | Operations Phase |  | √
| 31-90 00 00 | Closure Phase
Overview
Scope
The scope of this exchange requirement is the exchange of Building Automation System (BAS) design information between other project design roles. The BAS components should be designed using BACnet protocol including objects, attributes and services. The exchange requirement also includes the need for shape, size and location of components.
General Discription
This exchange requirement allows BAS component information represented in IFC standards to be shared among various project design roles including architects, structural engineer and MEP engineers. The BAS component information can also be shared throughout several design interactions from conceptual design to production information. The BAS components should be designed using BACnet protocol including objects, attributes and services. The exchange requirement also includes the need for shape and location of components.
Information Description
Information provided through this exchange requirement includes: • BAS components objects, attributes • Shape representation of components • Location and orientation of occurrences of components

## example object
Properties of the Analog Input Object Type |  |  | Information Unit | Entity/Pset/Functional Part | Man | Rec | Opt | Mapped Concept
Property Identifier | Property Datatype | Conformance Code
Object_Identifier | BACnetObjectIdentifier | R | Object Geometric Representation | IfcProduct.Representation->IfcProductDefinitionShape |  | √ |  | Box Geometry; FootPrint Annotation Geometry
Object_Name | CharacterString | R | Object Placement | IfcProduct.ObjectPlacement->IfcObjectPlacement |  | √ |  | Product local placement
Object_Type | BACnetObjectType | R | Object Contained in Space | IfcElement.ContainedInStructure ->IfcRelContainedInSpatialStructure |  | √ |  | Spatial Containment
Present_Value | REAL | R | Object Connected From | IfcElement.ConnectedFrom->IfcRelConnectsElements |  | √ |  | Path Connectivity
Status Flags | BACnetStatusFlags | R | Decomposes | IfcObjectDefinition.Decomposes->IfcRelAggregates |  | √ |  | Object Definition Composition
Event State | BACnetEventState | R | Object Identifier | IfcControllort.GlobalId->IfcGloballyUniqueId | √ |  |  | Software Identity
Out of Service | BOOLEAN | R | Object Name | IfcControllor.Name->IfcLable | √ |  |  | Object User Identity
Units | BACnetEngineeringUnits | R | Object Type | IfcController.PredefinedType->IfcControllerTypeEnum | √ |  |  | BACnet Controllor Predefined Type; Object Predefined Type
… | … | … | Present Value | Pset_ControllerTypeMultiPosition.Value->IfcInteger | √ |  |  | PropertySets for Objects
|  |  | Description | IfcRoot.Description->IfcText |  |  | √ | -
Description | CharacterString | O | Status Flags | Pset_BACnetAnalogInputObject.StatusFlags ->IfcLabel:: PEnum_BACnetStatusFlag | √ |  |  | PropertySets for Objects
Device_Type | CharacterString | O | Event State | Pset_BACnetAnalogInputObject.EventState ->IfcLabel:: PEnum_BACnetEventState | √ |  |  | PropertySets for Objects
Property List | BACnetPropertyIdentifier | R | Out of Service | Pset_BACnetAnalogInputObject.OutOfService ->IfcBoolean | √ | ` |  | PropertySets for Objects
|  |  | Units | Pset_BACnetAnalogInputObject.Units ->IfcLabel | √ |  |  | PropertySets for Objects
|  |  | Property List | IfcPropertySet.HasPropertites->IfcProperty | √ |  |  | PropertySets for Objects

## Sheet3
Information Unit |  | Description | Entity/Pset/Functional Part | Man | Rec | Opt | Mapped Concept
BACnet Analog Input Object Type |  |  | IfcController
| Object Geometric Representation | Geometric representation of the object | IfcProduct.Representation->IfcProductDefinitionShape |  | √ |  | Box Geometry; FootPrint Annotation Geometry
| Object Placement | placement of the object | IfcProduct.ObjectPlacement->IfcObjectPlacement |  | √ |  | Product local placement
| Object Contained in Space | the object contained in space | IfcElement.ContainedInStructure ->IfcRelContainedInSpatialStructure |  |  | √ | Spatial Containment
| Object Connected From | other objects connection | IfcElement.ConnectedFrom ->IfcRelConnectsElements |  |  | √ | Path Connectivity
| Decomposes | which device is the object decomposed by | IfcObjectDefinition.Decomposes->IfcRelAggregates |  |  | √ | Element Composition
| Object Identifier | This property, of type BACnetObjectIdentifier, is a numeric code that is used to identify the object. It shall be unique within the BACnect device that maintains it | IfcControllort.GlobalId->IfcGloballyUniqueId | √ |  |  | -
| Object Name | This property, of type CharacterString, shall represent a name for the object that is unique within the BACnet device that maintains it. The minimum length of the string shall be one character. The set of characters used in the Object_Name shall be restricted to printable characters | IfcControllor.Name->IfcLable | √ |  |  | -
| Object Type | Indicates membership in a particular object type class. The value of this property shall be ANALOG_INPUT,Predefined Type =MULTIPOSITION | IfcController.PredefinedType->IfcControllerTypeEnum | √ |  |  | BACnet Controllor Predefined Type; Object Predefined Type
| Present Value | This property, of type REAL, indicates the current value, in engineering units, of the input being measured. ThePresent_Value property shall be writable when Out_Of_Service is TRUE | Pset_ControllerTypeMultiPosition.Value->IfcInteger | √ |  |  | PropertySets for Objects
| Description | Other description of object | IfcRoot.Description->IfcText |  |  | √ | -
| Status Flags | This property, of type BACnetStatusFlags, represents four Boolean flags that indicate the general “health” of object. PEnum_BACnetStatusFlagsEnum = ENUMERATION OF( IN_ALARM, FAULT, OVERRIDEN, OUT_OF_SERVICE); | Pset_BACnetAnalogInputObject.StatusFlags ->IfcLabel:: PEnum_BACnetStatusFlag | √ |  |  | PropertySets for Objects
| Event State | The Event_State property, of type BACnetEventState, is included in order to provide a way to determine whether this object has an active event state associated with it. PEnum_BACnetEventStateEnum = ENUMERATION OF( NORMAL, OFFNORMAL, FAULT); | Pset_BACnetAnalogInputObject.EventState ->IfcLabel:: PEnum_BACnetEventState | √ |  |  | PropertySets for Objects
| Out of Service | The Out_Of_Service property, of type BOOLEAN, is an indication whether (TRUE) or not (FALSE) the physical input that the object represents is not in service. | Pset_BACnetAnalogInputObject.OutOfService ->IfcBoolean | √ | ` |  | PropertySets for Objects
| Units | This property, of type BACnetEngineeringUnits, indicates the measurement units of this object. | Pset_BACnetAnalogInputObject.Units ->IfcLabel | √ |  |  | Unit Assignment; PropertySets for Objects
| Property List | This read-only property is a BACnetARRAY of property identifiers, one property identifier for each property that exists within the object. | IfcPropertySet.HasPropertites->IfcProperty | √ |  |  | PropertySets for Objects
| Tags | tags related to the object | IfcElement.Tag->IfcIdentifier |  |  | √ | Element Occurrence Attributes