## DC Annual Consumption
| AL Mutlaa District Cooling | Anuual Consumption
| Cost Calculatons | (Local Consultation Guide)
Annual Water Portable (1000 gallons/MWh) |  | 0.44 | of Annual Cooling Load MWh |  | AL Mutlaa District Cooling Design Report
Annual sewage Water (1000 gallons/MWh) |  | 0.11 | of Annual Cooling Load MWh District Cooling Guide 0.25 portable water
Annual treated sewage Water (1000 gallons/MWh) |  | 0.66 | of Annual Cooling Load Ton-h 1.5*(0.44/MWh) |  |  | AL Mutlaa District Cooling Design Report
Chemical Annual Cost |  | 0.0025 | $/ Annual Cooling Load Ton-h
Water Cost (1000 gallons) |  | 2.63 | $/(1000 gallons)
Sewer Cost (1000 gallons) |  | 2.63 | $/(1000 gallons)
Annual Cooling Load Demand/Villa |  | 25122 | Ton -h/year
Annual Cooling Load Demand/Villa |  | 87928 | kWh/year
Peak Cooling Load Demand/Villa |  |  | Ton | 45
Peak Cooling Load Demand/Villa |  |  | kW | 158
Peak Electric Load/Villa |  | 29 | kW
Annual Electric Load / Villa |  | 15.987 | MWh | (COP=5.5)
No. of Villas/ (N: Neighbourhood) |  | 2300
Electric | Rate | 0.118 | $/kWh
Annual Cooling Load Demand (N) |  | 278805540 | Ton -h/year
Annual Cooling Load Demand (N) |  | 975819.389 | MWh/year
Peak Cooling Load Installed (N) Ton |  | 83588.8 | Ton
Peak Cooling Load Installed (N) MW |  | 292.56 | MW
Peak Electric Load (N) |  | 74 | MW
Annual Chiller O&M Cost |  | 50 | $/ Cooling Load installed Ton
Annual Insurance |  | 0.003 | of the total construction cost
Annual Engineer labor cost |  | 0 | Included in chiller O&M cost
Annual Technician labor cost |  | 0 | Included in chiller O&M cost
Total Facility construction cost |  | 210014960 | Current Work
Annual | Utility Consumption Summary for N6
Electrical | (MWh) | 261210
Water (1000 gallons) |  | 429360.5312
Sewer (1000 gallons) |  | 107340.1328
Estimate | of Annual Maintenancce and Utility Cost
Electric Utility Cost ($) |  | 30822780
Estimated Water Cost ($) |  | 1129218.197
Estimated Sewer Cost ($) |  | 282304.5492
Estimated Chemicals Cost ($) |  | 697013.85
Operator Salaries |  | 0
Chiller Operation & Maintenance Cost |  | 4179440
Annual Insurance |  | 630044.88
Total Annual Cost |  | 37740801.4762
Total Annual Cost (no electricty) |  | 6918021.4762

## DC Capital Cost
DC Cost Estimate For Nieghbourhood Primary Plant Facilities and Distribution Network
AL Mutlaa District Cooling Design Report
Cost of the Plant Facility per MW Cooling Load | 1500 | $/Ton
Peak Cooling load Installed Per Nieghbourhood | 83588.8 | Ton
Cost of the Primary Plant Facility Per Nieghbourhood | 125.3832 | M$ | 1500 Ton Chiller 12+1
5651 kW
Distribution Pipe Network Cost Estimate
Diameter | Unit Rate | Length | Cost*
(mm) | $/m | m | m$
1200 | 2722.5 | 6000 | 16.335
750 | 1881 | 3000 | 5.643
350 | 1155 | 16000 | 18.48
200 | 858 | 32000 | 27.456
|  | Total | 67.914
ETU | 200 | 83588.8 | 16.7178
Total Facitility & Pipe Network cost M$ |  |  | 210.015
* Civils Cost Excluded - assumed is provided as
part of city wide infrastructure costs

## VRF Capital & Running Cost
VRF Captial & Running Cost Estimate For one Nieghbourhood
|  |  | 1st 12 Years | 2nd 12 Years
Number of Units per Villa |  | 4
Number of Villas Per Nieghbourhood |  | 2300
Load per Unit (Ton) |  | 10
Cost of the Unit ($/Ton) | 2700 |  | 2700 | 3227.1691
Inflation Rate 1.5% | 0.015 |  | 0.015 | 0.015
Interest Rate |  |  | 0.03 | 0.04
Captial Cost Per Nieghbourhood | 4.05e-05 |  | 124200000 | 148449776.8955
Annual Maintenance & Labor & Spare Parts Cost
Annual Maintenance & Labor & Spare Parts Cost $/ Year-Ton |  | 40
VRF Annual Running Cost (no electricty) |  | 3680000

## DX Capital & Running Cost
DX Captial & Running Cost Estimate For one Nieghbourhood
|  |  | 1st 8 Years | 2nd 8 Years | 3rd 8 Years
Number of Units per Villa |  | 8
Number of Villas Per Nieghbourhood |  | 2300
Load per Unit (Ton) |  | 6.5
Cost of the Unit ($/Ton) | 2700 |  | 600 | 674.8956 | 760.3913
Inflation Rate 1.5% | 0.015 |  | 0.015 | 0.015 | 0.015
Interest Rate |  |  | 0.03 | 0.04 | 0.05
Captial Cost Per Nieghbourhood | 4.05e-05 |  | 35880000 | 40358754.007 | 45471401.4498
Annual Maintenance & Labor & Spare Parts Cost
Annual Maintenance & Labor & Spare Parts Cost $/ Year-Ton |  | 24
DX Annual Running Cost (no electricty) |  | 2870400

## 24 Years Cost of DC
DC 24 Years Total Cost of one Neighbor (Villas Only)
Peak Electric Load MW |  | 74 |  | Annual Electric Load MWH | 261210
DC Annual Running Cost (no electricty) |  | 6918021.4762 |  | DC System Cost | 210014960
Power Station Cost/MW |  | 1335774 |  | Power Station Cost | 98847276
Power Station M&O Cost /MWH |  | 4 |  | Power Station M&O Cost /Year | 1044840
Power Station Labor Cost /MWH |  | 17.358 |  | Power Station Labor Cost/Year | 4534083.18
Power Station Insurance Cost % of toal cost |  | 0.0075 |  | Power Station Insurance Cost/Year | 741354.57
Electric Utility Cost/MW |  | 117.68 |  | Electric Utility Cost/Year | 30739192.8
Interest Rate 3% |  | 0.03 |  | Inflation Rate 1.5% | 0.015
Power Station Cost/Year |  | 5836676.2214 |  | DC System Cost/Year | 12400840.6986
| Power Station | Insurance | Electric Utility | System | Running
Years | Power Station Cost | Power Station Insurance Cost | Electric Utility Cost | DC System Cost | DC Running Cost | Total Cost/Year | Yearly Total Cost for 12 N M$ | Accumalted Yearly Total Cost for 12 N M$
1 | 5836676.2214 | 741354.57 | 30739192.8 | 210014960 | 6918021.4762 | 254250206.0676 | 3051.0025 | 3051.0025
2 | 5836676.2214 | 752474.8885 | 31200280.692 |  | 7021791.7983 | 44811225.6003 | 537.7347 | 3588.7372
3 | 5836676.2214 | 763762.0119 | 31668284.9024 |  | 7127118.6753 | 45395844.811 | 544.7501 | 4133.4873
4 | 5836676.2214 | 775218.4421 | 32143309.1759 |  | 7234025.4554 | 45989229.2948 | 551.8708 | 4685.3581
5 | 5836676.2214 | 786846.7187 | 32625458.8136 |  | 7342535.8373 | 46591517.5909 | 559.0982 | 5244.4563
6 | 5836676.2214 | 798649.4195 | 33114840.6958 |  | 7452673.8748 | 47202840.2114 | 566.4341 | 5810.8904
7 | 5836676.2214 | 810629.1608 | 33611563.3062 |  | 7564463.9829 | 47823332.6713 | 573.88 | 6384.7704
8 | 5836676.2214 | 822788.5982 | 34115736.7558 |  | 7677930.9427 | 48453132.518 | 581.4376 | 6966.2079
9 | 5836676.2214 | 835130.4271 | 34627472.8071 |  | 7793099.9068 | 49092379.3625 | 589.1086 | 7555.3165
10 | 5836676.2214 | 847657.3836 | 35146884.8992 |  | 7909996.4054 | 49741214.9096 | 596.8946 | 8152.2111
11 | 5836676.2214 | 860372.2443 | 35674088.1727 |  | 8028646.3515 | 50399782.9899 | 604.7974 | 8757.0085
12 | 5836676.2214 | 873277.828 | 36209199.4953 |  | 8149076.0468 | 51068229.5915 | 612.8188 | 9369.8272
13 | 5836676.2214 | 886376.9954 | 36752337.4877 |  | 8271312.1875 | 51746702.892 | 620.9604 | 9990.7877
14 | 5836676.2214 | 899672.6503 | 37303622.5501 |  | 8395381.8703 | 52435353.2921 | 629.2242 | 10620.0119
15 | 5836676.2214 | 913167.7401 | 37863176.8883 |  | 8521312.5984 | 53134333.4481 | 637.612 | 11257.6239
16 | 5836676.2214 | 926865.2562 | 38431124.5416 |  | 8649132.2873 | 53843798.3065 | 646.1256 | 11903.7495
17 | 5836676.2214 | 940768.235 | 39007591.4098 |  | 8778869.2716 | 54563905.1378 | 654.7669 | 12558.5163
18 | 5836676.2214 | 954879.7585 | 39592705.2809 |  | 8910552.3107 | 55294813.5716 | 663.5378 | 13222.0541
19 | 5836676.2214 | 969202.9549 | 40186595.8601 |  | 9044210.5954 | 56036685.6318 | 672.4402 | 13894.4943
20 | 5836676.2214 | 983740.9992 | 40789394.798 |  | 9179873.7543 | 56789685.773 | 681.4762 | 14575.9706
21 | 5836676.2214 | 998497.1142 | 41401235.72 |  | 9317571.8606 | 57553980.9162 | 690.6478 | 15266.6183
22 | 5836676.2214 | 1013474.5709 | 42022254.2558 |  | 9457335.4385 | 58329740.4867 | 699.9569 | 15966.5752
23 | 5836676.2214 | 1028676.6895 | 42652588.0696 |  | 9599195.4701 | 59117136.4506 | 709.4056 | 16675.9809
24 | 5836676.2214 | 1044106.8399 | 43292376.8907 |  | 9743183.4022 | 59916343.3541 | 718.9961 | 17394.977
Total | 140080229.3135 | 21227591.4968 | 880171316.2686 | 210014960 | 198087311.8006 | 1449581408.8794 | 17394.977 | 17394.9769
| 1680962751.7617 | 254731097.9611 | 10562055795.2227 | 2520179520 | 2377047741.6067 | 17394976906.5522 | 208739.7237 | 208739.7229

## Graph 24 Yers DC
24 Years DC Cooling System
One Neighbor (Villas Only)
Power Station | Power Station Insurance | Electric Utility | DC System Cost | DC Running Cost
140080229.3135 | 21227591.4968 | 880171316.2686 | 210014960 | 198087311.8006

## Graph 24 Years DC-1
Consumption (kWh)
Jan | 3485.2
Feb | 3545.4
Mar | 4921.0414
Apr | 10240.34
May | 18687.8
Jun | 21483.3
Jul | 23623.4
Aug | 22711.6
Sep | 17835.1
Oct | 13582.9
Nov | 7323.6
Dec | 4141.5
Total | 151581.1814
EUI | 181.8392
| Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec | Total | kWh/m2 | %
Power Station | 333.3 | 904.2 | 1929.2336 | 7339.97 | 15343.9 | 18404.2 | 21105.8 | 20408.1 | 15686.4 | 11050.7 | 4474.8 | 862.8 | 117843.4036 | 141.3668 | 9.6635
Power Station Insurance | 1463.1 | 1159.5 | 1045.0424 | 960.74 | 1132.8 | 997.6 | 978.6 | 940.2 | 918.6 | 1032.4 | 1038.5 | 1083.9 | 12750.9824 | 15.2963 | 1.4644
Electric Utility | 1358.2 | 1302.3 | 1707.205 | 1491.93 | 1356.4 | 1125.8 | 282.3 | 73.5 | 70.9 | 1269.5 | 1582.6 | 2023.2 | 13643.835 | 16.3674 | 60.719
DC System Cost | 330.6 | 179.4 | 239.5604 | 447.7 | 854.7 | 955.7 | 1256.7 | 1289.8 | 1159.2 | 230.3 | 227.7 | 171.6 | 7342.9604 | 8.8087 | 14.488
DC Running Cost | 3485.2 | 3545.4 | 4921.0414 | 10240.34 | 18687.8 | 21483.3 | 23623.4 | 22711.6 | 17835.1 | 13582.9 | 7323.6 | 4141.5 | 151581.1814 | 181.8392 | 13.6651
kWh/m2 | 4.1809 | 4.2531 | 5.9034 | 12.2845 | 22.4182 | 25.7717 | 28.339 | 27.2452 | 21.3953 | 16.2943 | 8.7855 | 4.9682 | 181.8392

## 24 Years Cost of VRF
VRF 24 Years Total Cost of one Neighbor (Villas Only)
[6 empty] | 1st 12 Years | 2nd 12 Years
Peak Electric Load MW |  | 144.8 |  | Annual Electric Load MWH | 309255
VRF Annual Running Cost (no electricty) |  | 3680000 |  | VRF System Cost |  | 124200000 | 148449776.8955
Power Station Cost/MW |  | 1335774 |  | Power Station Cost | 193420075.2
Power Station M&O Cost /MWH |  | 4 |  | Power Station M&O Cost /Year | 1237020
Power Station Labor Cost /MWH |  | 17.358 |  | Power Station Labor Cost/Year | 5368048.29
Power Station Insurance Cost % of toal cost |  | 0.0075 |  | Power Station Insurance Cost/Year | 1450650.564
Electric Utility Cost/MW |  | 117.68 |  | Electric Utility Cost/Year | 36393128.4
Interest Rate 3% |  | 0.03 |  | Inflation Rate 1.5% | 0.015 | 0.03 | 0.04
Power Station Cost/Year |  | 11420955.6332 |  | VRF Cost/Year |  | 12477391.0157 | 15817646.263
Years | Power Station Cost | Power Station Insurance Cost | Electric Utility Cost | VRF System Cost | VRF Running Cost | Total Cost/Year | Yearly Total Cost for 12 N M$ | Accumalted Yearly Total Cost for 12 N M$
1 | 11420955.6332 | 1450650.564 | 36393128.4 | 124200000 | 3680000 | 177144735.5972 | 2125.7368 | 2125.7368
2 | 11420955.6332 | 1472410.3225 | 36939025.326 |  | 3735200 | 53567593.2817 | 642.8111 | 2768.5479
3 | 11420955.6332 | 1494496.4773 | 37493110.7059 |  | 3791228 | 54199790.8164 | 650.3975 | 3418.9454
4 | 11420955.6332 | 1516913.9245 | 38055507.3665 |  | 3848096.42 | 54841477.3442 | 658.0977 | 4077.0432
5 | 11420955.6332 | 1539667.6333 | 38626339.977 |  | 3905817.8663 | 55492786.1098 | 665.9134 | 4742.9566
6 | 11420955.6332 | 1562762.6478 | 39205735.0766 |  | 3964405.1343 | 56153864.492 | 673.8464 | 5416.803
7 | 11420955.6332 | 1586204.0875 | 39793821.1028 |  | 4023871.2113 | 56824859.0348 | 681.8983 | 6098.7013
8 | 11420955.6332 | 1609997.1489 | 40390728.4193 |  | 4084229.2795 | 57505918.4809 | 690.071 | 6788.7723
9 | 11420955.6332 | 1634147.1061 | 40996589.3456 |  | 4145492.7187 | 58197184.8036 | 698.3662 | 7487.1385
10 | 11420955.6332 | 1658659.3127 | 41611538.1858 |  | 4207675.1095 | 58898828.2411 | 706.7859 | 8193.9245
11 | 11420955.6332 | 1683539.2024 | 42235711.2586 |  | 4270790.2361 | 59610996.3303 | 715.332 | 8909.2564
12 | 11420955.6332 | 1708792.2904 | 42869246.9275 |  | 4334852.0896 | 60333858.9407 | 724.0063 | 9633.2627
13 | 11420955.6332 | 1734424.1748 | 43512285.6314 | 148449776.8955 | 4399874.871 | 209517330.2058 | 2514.208 | 12147.4707
14 | 11420955.6332 | 1760440.5374 | 44164969.9158 |  | 4465872.994 | 61812239.0805 | 741.7469 | 12889.2176
15 | 11420955.6332 | 1786847.1454 | 44827444.4646 |  | 4532861.089 | 62568108.3322 | 750.8173 | 13640.0349
16 | 11420955.6332 | 1813649.8526 | 45499856.1315 |  | 4600854.0053 | 63335331.6227 | 760.024 | 14400.0588
17 | 11420955.6332 | 1840854.6004 | 46182353.9735 |  | 4669866.8154 | 64114031.0225 | 769.3684 | 15169.4272
18 | 11420955.6332 | 1868467.4194 | 46875089.2831 |  | 4739914.8176 | 64904427.1534 | 778.8531 | 15948.2803
19 | 11420955.6332 | 1896494.4307 | 47578215.6224 |  | 4811013.5399 | 65706679.2262 | 788.4802 | 16736.7605
20 | 11420955.6332 | 1924941.8472 | 48291888.8567 |  | 4883178.743 | 66520965.0801 | 798.2516 | 17535.0121
21 | 11420955.6332 | 1953815.9749 | 49016267.1896 |  | 4956426.4241 | 67347465.2218 | 808.1696 | 18343.1816
22 | 11420955.6332 | 1983123.2145 | 49751511.1974 |  | 5030772.8205 | 68186362.8656 | 818.2364 | 19161.418
23 | 11420955.6332 | 2012870.0627 | 50497783.8654 |  | 5106234.4128 | 69037843.9741 | 828.4541 | 19989.8721
24 | 11420955.6332 | 2043063.1137 | 51255250.6233 |  | 5182827.929 | 69902097.2992 | 838.8252 | 20828.6973
Total | 274102935.1972 | 41537233.091 | 1042063398.8463 | 272649776.8955 | 105371356.5266 | 1735724700.5565 |  | 20828.6964
| 3289235222.366 | 498446797.0915 | 12504760786.1552 | 3271797322.7463 | 1264456278.319 | 20828696406.6781 | 0 | 249944.3569

## Graph 24 Yers VRF
24 Years VRF Cooling System
One Neighbor (Villas Only)
Power Station | Power Station Insurance | Electric Utility | VRF System Cost | VRF Running Cost
274102935.1972 | 41537233.091 | 1042063398.8463 | 272649776.8955 | 105371356.5266

## 24 Years Cost of DX
DX 24 Years Total Cost of one Neighbor (Villas Only)
[6 empty] | 1st 8 Years | 2nd 8 Years | 3rd 8 Years
Peak Electric Load MW |  | 146.8 |  | Annual Electric Load MWH | 405135.8
DX Annual Running Cost (no electricty) |  | 2870400 |  | DX System Cost |  | 35880000 | 40358754.007 | 45471401.4498
Power Station Cost/MW |  | 1335774 |  | Power Station Cost | 196091623.2
Power Station M&O Cost /MWH |  | 4 |  | Power Station M&O Cost /Year | 1620543.2
Power Station Labor Cost /MWH |  | 17.358 |  | Power Station Labor Cost/Year | 7032347.2164
Power Station Insurance Cost % of toal cost |  | 0.0075 |  | Power Station Insurance Cost/Year | 1470687.174
Electric Utility Cost/MW |  | 117.68 |  | Electric Utility Cost/Year | 47676380.944
Interest Rate 3% |  | 0.03 |  | Inflation Rate 1.5% | 0.015 | 0.03 | 0.04 | 0.05
Power Station Cost/Year |  | 11578703.6392 |  | DX Cost/Year | 0 | 5111335.2311 | 5994398.2368 | 7035417.7005
Years | Power Station Cost | Power Station Insurance Cost | Electric Utility Cost | DX System Cost | DX Running Cost | Total Cost/Year | Yearly Total Cost for 12 N M$ | Accumalted Yearly Total Cost for 12 N M$
1 | 11578703.6392 | 1470687.174 | 47676380.944 | 35880000 | 2870400 | 99476172.7572 | 1193.7141 | 1193.7141
2 | 11578703.6392 | 1492747.4816 | 48391526.6582 |  | 2913456 | 64376435.779 | 772.5172 | 1966.2313
3 | 11578703.6392 | 1515138.6938 | 49117399.558 |  | 2957157.84 | 65168399.7311 | 782.0208 | 2748.2521
4 | 11578703.6392 | 1537865.7742 | 49854160.5514 |  | 3001515.2076 | 65972249.1724 | 791.667 | 3539.9191
5 | 11578703.6392 | 1560933.7609 | 50601972.9597 |  | 3046537.9357 | 66788153.2954 | 801.4578 | 4341.3769
6 | 11578703.6392 | 1584347.7673 | 51361002.5541 |  | 3092236.0047 | 67616295.9653 | 811.3956 | 5152.7725
7 | 11578703.6392 | 1608112.9838 | 52131417.5924 |  | 3138619.5448 | 68456860.7602 | 821.4823 | 5974.2548
8 | 11578703.6392 | 1632234.6785 | 52913388.8563 |  | 3185698.838 | 69310034.012 | 831.7204 | 6805.9752
9 | 11578703.6392 | 1656718.1987 | 53707089.6891 | 40358754.007 | 3233484.3206 | 110534749.8546 | 1326.417 | 8132.3922
10 | 11578703.6392 | 1681568.9717 | 54512696.0344 |  | 3281986.5854 | 71054955.2307 | 852.6595 | 8985.0517
11 | 11578703.6392 | 1706792.5063 | 55330386.475 |  | 3331216.3842 | 71947099.0046 | 863.3652 | 9848.4169
12 | 11578703.6392 | 1732394.3939 | 56160342.2721 |  | 3381184.6299 | 72852636.9351 | 874.2316 | 10722.6485
13 | 11578703.6392 | 1758380.3098 | 57002747.4062 |  | 3431902.3994 | 73771746.7545 | 885.261 | 11607.9095
14 | 11578703.6392 | 1784756.0144 | 57857788.6173 |  | 3483380.9354 | 74704629.2062 | 896.4556 | 12504.365
15 | 11578703.6392 | 1811527.3546 | 58725655.4465 |  | 3535631.6494 | 75651518.0897 | 907.8182 | 13412.1832
16 | 11578703.6392 | 1838700.265 | 59606540.2782 |  | 3588666.1241 | 76612626.3065 | 919.3515 | 14331.5348
17 | 11578703.6392 | 1866280.7689 | 60500638.3824 | 45471401.4498 | 3642496.116 | 123059520.3563 | 1476.7142 | 15808.249
18 | 11578703.6392 | 1894274.9805 | 61408147.9581 |  | 3697133.5577 | 78578260.1355 | 942.9391 | 16751.1881
19 | 11578703.6392 | 1922689.1052 | 62329270.1775 |  | 3752590.5611 | 79583253.483 | 954.999 | 17706.1872
20 | 11578703.6392 | 1951529.4417 | 63264209.2302 |  | 3808879.4195 | 80603321.7306 | 967.2399 | 18673.427
21 | 11578703.6392 | 1980802.3834 | 64213172.3686 |  | 3866012.6108 | 81638691.002 | 979.6643 | 19653.0913
22 | 11578703.6392 | 2010514.4191 | 65176369.9541 |  | 3924002.8 | 82689590.8124 | 992.2751 | 20645.3664
23 | 11578703.6392 | 2040672.1354 | 66154015.5035 |  | 3982862.842 | 83756254.12 | 1005.075 | 21650.4415
24 | 11578703.6392 | 2071282.2174 | 67146325.736 |  | 4042605.7846 | 84838917.3772 | 1018.067 | 22668.5085
Total | 277888887.3408 | 42110951.7801 | 1365142645.2032 | 121710155.4569 | 82189658.0907 | 1889042297.8716 |  | 22668.5076
| 3334666648.0893 | 505331421.3608 | 16381711742.4379 | 1460521865.4825 | 986275897.0889 | 22668507574.4593 | 0 | 272022.0909

## Graph 24 Yers DX
30 Years DX Cooling System
One Neighbor (Villas Only)
Power Station | Power Station Insurance | Electric Utility | DX System Cost | DX Running Cost
277888887.3408 | 42110951.7801 | 1365142645.2032 | 121710155.4569 | 82189658.0907

## 24Years Cost of 3 Alertinatives
24 Years Cost Comparison of the Three Alternatives
AL Mutlaa City (Villas Only) | 12 Neighbors | (12*2300)
| DC Cooling System | VRF Cooling System | DX Cooling System
Cost of Power Station Purchasing (M$) | 1680.9628 | 3289.2352 | 3334.6666
Power Station Insurance Cost (m$US) | 254.7311 | 498.4468 | 505.3314
Electric Utility Cost (M$) | 10562.0558 | 12504.7608 | 16381.7117
Capital Cost ( M$) | 2520.1795 | 3271.7973 | 1460.5219
Running Cost (M$) (No Electricity) | 2377.0477 | 1264.4563 | 986.2759
24Yeas Total Cost (M$) | 17394.9769 | 20828.6964 | 22668.5076
Cost of Power Station & Insurance (M$) | 1935.6938 | 3787.682 | 3839.9981
Peak Electric Power Demand (MW)

## Graph 24 Yeas Total Cost
DX | VRF | DC
6805.9752 | 6788.7723 | 6966.2079
14331.5348 | 14400.0588 | 11903.7495
22668.5076 | 20828.6964 | 17394.9769
8 Years | 16 Years | 24 Years | Years
6805.9752 | 14331.5348 | 22668.5076 | DX
6788.7723 | 14400.0588 | 20828.6964 | VRF
6966.2079 | 11903.7495 | 17394.9769 | DC

## Graph Cost of Power Station &
DX | VRF | DC
3839.9981 | 3787.682 | 1935.6938

## Graph Peak Electric Power Deman
DX | VRF | DC
1761.6 | 1737.6 | 888

## Graph Electrical Utility Cost
DX | VRF | DC
16381.7117 | 12504.7608 | 10562.0558

## Graph Annual CO2 Emission
CO2 emission is based on plant emission factor (Kuwait) of 870 gCO2/kWhe
DX | VRF | DC | 0.87 | kg/kWh
405135.8 | 309255 | 261210 | Annual Electric Load MWH
352468.146 | 269051.85 | 227252.7 | Annual CO2 emission Kg